Substitutes for Potent Greenhouse Gases (HFCs, PFCs and SF6)

1998

Final Report

Per Henrik Pedersen

MSc.Eng

Danish Technological Institute

Energy

DTI Energy

P.O. Box 141

DK-2630 Taastrup

Tel.: +45 43 50 45 23

Fax:  +45 43 50 72 22

E-mail: Per.Henrik.Pedersen@dti.dk

Contents

Preface 5

1	Background 9

2	Aim of project and organisation 13

3   Application of HFC substances and possible alternatives 17

3.1	Refrigeration industry 17

3.1.1	Domestic refrigerators and freezers 18

3.1.2	Commercial refrigerators and freezers 23

3.1.3	Commercial refrigeration systems 23

3.1.4	Industrial refrigeration plants 30

3.1.5	Mobile refrigeration systems 30

3.1.6	Heat pumps 32

3.1.7	Air-conditioning systems 33

3.1.8	Cryogenic systems 34

3.2	Polyurethane foam 35

3.2.1	Insulating foam 35

3.2.2	Jointing foam 38

3.2.3	Flexible polyurethane foam 39

3.3	Fire extinguishants 39

3.4	Propellant in aerosol cans and foghorns 40

3.5	Other fields of application 41

4	Use of PFC substances 43

4.1	PFC in refrigerant mixtures 43

4.2	Other applications of PFC substances 44

5   Consumption of SF6 and substitution possibilities 47

5.1	Noise-reducing double glazed windows 47

5.2	Protective gases in light-metal foundries 49

5.3	Insulating gas in electric power switches 50

5.4	Tracer gas and other laboratory purposes 51

5.5	Car tyres 52

5.6	Other possible applications of SF6 52

6	Evaluations and recommendations 55

8	Literature 59

Appendix A: List over refrigerants and refrigerant mixtures 61

Appendix B: Commercial refrigeration systems 63

Appendix C:  Sabroe Chillers with NH3-refrigerant, installed in Denmark 1990-1998 73

Appendix D: Gram Chillers (York International) with NH3 refrigerant, installed in Denmark 1992-1998 77

Appendix E: Bonus Chillers with Hydrocarbon-refrigerant, installed in Sweden 1996-1998 79

# Preface

In recent years, the consumption of potent greenhouse gases in Denmark has increased, whilst at the same time the consumption of CFCs, HCFCs and other substances, depleting the ozone layer, is approaching zero.

Substitution for CFCs and HCFCs

Especially the consumption of HFC-substances has increased. These substances are used as substitutes for CFCs and HCFCs for certain purposes, especially for refrigeration and blowing of polyurethane foam. However, it should be mentioned that more environmentally friendly alternatives have been introduced, e.g. hydrocarbons in aerosol cans, cyclopentane for district heating pipes and hydrocarbons, ammonia and water in various types of refrigeration systems.

Artificial substances

CFCs (halogenated chlorofluorocarbons), HCFCs (hydrochlorofluorocar-

bons), HFCs (hydrofluorocarbons), PFCs (fluorocarbons) and SF6 (sulphur hexafluoride) are all artificial substances which were not to be found in nature until recently.

Ozone depleting substances

Furthermore, as these substances are relatively stable, their lifetime in the atmosphere is long. This applies particularly to the fully halogenated substances: CFCs, PFCs and SF6. The CFCs and HCFCs are ozone depleting substances, which are subjected to an international convention, the Montreal Protocol, for guarantee of elimination of these substances. Except essential uses, Danish and EU legislation has now prohibited the use of CFCs. Additionally, the use of HCFC is decreasing in Denmark and will be brought to a complete stop before year 2002. After December 31st 1999, the erection of new plants using HCFC is forbidden.

United Nation Climate Convention

Because HFCs, PFCs and SF6 contain neither chlorine nor bromide, these substances will not contribute to any depletion of the ozone layer. However, they contribute to the greenhouse effect. The United Nation Climate Convention conducted the regulation of greenhouse gases. The substances have been included in the list of greenhouse gases (in the Kyoto Protocol) and the countries have to reduce the emission of them. The substances are regarded as comparable to carbon dioxide (CO2), methane (CH4) and nitrous oxide (N2O).

Danish consumption

In 1997, Danish consumption of HFC substances amounted to app. 890 tonnes, where the corresponding amount of SF6 was app. 13 tonnes. If the entire amount of these substances was released to the atmosphere, the resulting impact would correspond to an increased emission of greenhouse gases, corresponding to app. 1.6 million tonnes of CO2 (the contribution would be 78% from the HFC substances, 18% from SF6 and 3% PFC). That corresponds to app. 3% of the Danish CO2 emission (57.3 million tonnes in 1997). In addition, some of the substances have a very long life in the atmosphere.

This it the reason why the Council for Re-use and Less Polluting Technologies has supported this project financially.

According to experience from the CFC programme it is possible to recover some CFC and send it to controlled destruction. From 1993 to 1996 the refrigeration industry, for instance, has returned a total amount of 163 tonnes of CFC refrigerant through the KMO organisation (Danish refrigeration industy’s recovery and recycling scheme). Most of this has been destroyed and a small amount has been purified and recycled afterwards. Similarly, it must be expected that some HFC refrigerants will be returned through the KMO organisation.

However, the recharge of refrigerant mixtures in the R400 series will involve certain difficulties as the original concentration of the mixture might have changed.

Phase-out strategy for HFCs

At an international conference for natural refrigerants held in September 1996, the Danish Minister of Environment and Energy, Mr. Svend Auken, proclaimed that an environmental phase-out strategy would be initiated for HFCs and other potent greenhouse gases in Denmark within a period of 10 years. At the same time, he asked the Danish Environmental Protection Agency (the Danish EPA) to investigate how the phase-out strategy could be carried out and also to initiate discussions about this topic with industry and the green organisations. This report forms part of the basis for the further discussion.

In addition, HFCs, PFCs and SF6  are registered on the Danish EPA’s list of non-desirable substances. It was published as an official list in 1998 (Environmental Review No. 7, Danish Environmental Protection Agency, 1998).

Technical discussions

In recent years, various technologies have been discussed at conferences and seminars, in technical magazines and in daily newspapers. Many questions have been asked about how to find the most suitable techno-logy that is environmentally safe and safe to use. Examples are modern household refrigerators using two kinds of refrigerants, viz. HFC-134a and hydrocarbon (isobutane).

Such discussions will presumably continue many years from now. It is not only a discussion between industry on the one side and green organisations on the other. It is to a high degree a discussion among people within different industrial trades and the discussions are often influenced by commercial considerations.

The Energy Division at Danish Technological Institute (DTI Energy) is aware that this report might be used as reference in such discussions. The steering committee, established by the Danish EPA on the basis of this project, consists of members representing both industry and green organisations.

The Danish EPA has assessed that matters related to this project shall be discussed freely in order to allow the members of the steering committee and their respective organisations to contribute with further information. DTI Energy will then attempt to depict all relevant and factual information.

However, development continually takes place within the various technological areas mentioned in this report. Therefore, some of the information will quickly become obsolete. Finally, there might be information DTI has no knowledge of and therefore it has not been mentioned in this report.

# 1	Background

Consumption

In 1997, Danish industry utilised app. 890 tonnes of HFCs, app. 13 tonnes of SF6 and app. 8 tonnes of PFCs.

The table below shows consumption and the environmental effects from using the substances.

| Sub- stance | Consumption in 1997, (in tonnes) | GWP (100 yrs ) | CO2 equivalents, (in tonnes) | Atmospheric Life Time, (in yrs) |
| --- | --- | --- | --- | --- |
| HFC-134a | 700 | 1300 | 910.000 | 14.6 |
| HFC-152a | 15 | 140 | 2100 | 1.5 |
| R-404A | 110 | 3260 | 358.600 | 36.6, 48.3 and 14.6 |
| Other HFC’s | 66 | various | (60.000) | various |
| SF6 | 13 | 23900 | 310.700 | 3200 |
| PFC (C3F8) | 8 | 7000 | 56.000 | 2600 |
| Total | 912 |  | 1.697.400 |  |

Notes: R404A is a mixture of HFC-125, HFC-143a and HFC-134a

(44%, 52%, 4%)

GWP (Global Warming Potential) for HFC-143a is 3800 and GWP for HFC-125 is 2800.

In comparison the definition of GWP = 1 for CO2

Figures showing the amount of consumption appear from a survey performed by the Danish EPA on ozone layer depleting substances and potent greenhouse gases (the Danish EPA, 1998). This report has been prepared by Jan Holmegaard Hansen and Tomas Sander Poulsen, COWI.

3% of CO2 emission

It appears that if the entire amount of these substances is released to the atmosphere, it will cause an increased emission of greenhouse gases, corresponding to app. 1.69 million tonnes, which is nearly 3% of the Danish CO2 emission (57.3 million tonnes in 1997, corrected for electricity export). It should be emphasised that the figure represents the consumption of raw materials and for that reason the potential emission of these substances. The actual emission will depend on the extent of recollection and successful destruction of the substances.

A substantial increase in the consumption of HFC substances has been registered. In some cases these substances are used as substitutes for CFCs and HCFCs. However, consumption in 1997 is at the same level as in 1996. In 1997, 1225 tonnes of HCFC were used in Danish industry and it can be expected that part of the consumption will be converted into HFC substances when the use of HCFC becomes prohibited in the year 2000/2002.

From an environmental point of view the use of HFC substances instead of CFCs and HCFCs is an improvement, because the impact on the ozone layer is eliminated. CFCs and HCFCs are also very strong greenhouse gases, but a certain amount of disagreement currently prevails about how the substances exactly contribute to the greenhouse effect.

The substances contribute with two contradicting effects: On the one hand they are very strong greenhouse gases with GWP values of 4000 (CFC-11), 8500 (CFC-12) and 1700 (HCFC-22). On the other hand, the substances contribute to the decomposition of stratospheric ozone, which also is a green house gas.

In addition, it should be mentioned that the contribution to the greenhouse effect for different HFC substances covers a wide field. For instance GWP values range from 140 (HFC-152a) to 11700 (HFC-23).

A substantial increase in the consumption of PFC substances is also expected because of an intensive sales campaign for a drop-in substitute for CFC-12 in refrigeration systems. This drop-in refrigerant contains a PFC substance with a high GWP factor and a very long atmospheric life (see chapter 5).

Achievements so far

Danish Environmental Protection Agency

By means of the now completed CFC programme (initiated by the Danish EPA) and the Cleaner Technology programme, various activities have been supported to encourage development of products and production processes that do not use HFC or other potent greenhouse gases.

In co-operation with industry various developments have been carried out, e.g. refrigerators and pre-insulated district heating pipes using hydrocarbons as blowing agent for insulating foam, apparatus for charging hydrocarbons in refrigerators, application of water and inert gases in fire extinguishers etc.

Natural refrigerants comprise the consumption of substances which already form part of nature’s own cycle, i.e. ammonia, hydrocarbons, CO2, water and air. Some of these refrigerants might be chemically produced, e.g. ammonia.

The Cleaner Technology activity that at present is in progress is called “Programme for Natural Refrigerants” and is carried out by DTI Energy in co-operation with a number of industrial companies. Several initiatives have already been put into action: development of methods to produce small ammonia refrigeration systems, a machine for production of ice slurry (a mixture of water, alcohol and ice, applicable as secondary refrigerant) and a preliminary project on cooling containers (reefers). In addition, a major international conference on natural refrigerants was held in Aarhus, Denmark in September 1996, and it received financial support from the Danish EPA.

Danish Energy Agency

In addition, the Danish Energy Agency supports the development of new energy saving refrigeration systems using natural refrigerants. The following projects can be mentioned: Development of a refrigerant plant, using water as refrigerant (the “LEGO-plant”), development of commercial refrigerators using hydrocarbons as refrigerants, application of ammonia as refrigerants in supermarkets and an ammonia cooling system as demonstration plant in a big city hotel.

It should be mentioned that the total consumption of CFC substances in the late 1980’s amounted to app. 6000 tonnes. Most of the previous applications of CFC have now been replaced by natural substances, i.e. hydrocarbons in aerosol cans, in insulating foam and in certain refrigeration systems, water for cleaning electronic components, ammonia in certain refrigeration systems, etc.

# 2	Aim of project and organisation

Aim of project

As far as the potent greenhouse gases HFCs, PFCs and SF6 are concerned, the aim of the project is to describe the following conditions within each field of application:

-	Application and consumption figures (from survey prepared by the Danish EPA)

-	Emission to surrounding environment / accumulation in products

-	Alternative technology, development steps and possible implementation in Denmark or abroad

-	Estimated costs by introduction of alternative technology and other obstacles for such introduction (machinery availability, energy consumption, safety rules, standards etc.)

-	Demand for a possible Cleaner Technology activity and description of such project

Information is collected by means of contacting relevant industrial enterprises, trade organisations in Denmark and abroad and green organisations. Supplementary information will be collected by means of attending technical conferences, amongst others within the field of refrigeration technology and PU-foam.

Practical possibilities

Such measurements will allow the environmental authorities and Danish industry to achieve a sound background for further estimation of the practical possibilities within technology, economy and safety for phasing-out potent greenhouse gases within different fields of application.

At the same time, a broad perspective of the areas requiring Cleaner Technology effort in order to develop new, more environmentally friendly technologies will be obtained.

Energy consumption

If introduction of alternative technologies will create a considerable change of the energy consumption, this will be specifically mentioned. Obviously, this is a very important factor. Possible increase of energy consumption very soon means reduction of the environmental advantages which have been achieved by phasing-out potent greenhouse gases within different fields of application. On the other hand energy savings might encourage further introduction of new technology.

Steering committee

The project is carried out by DTI Energy but has a steering committee appointed by the Danish EPA and comprises the following members:

Lise Emmy Jensen, Danish EPA (chairman of the first part of the project)

Frank Jensen, Danish EPA (chairman of the second part of the project)

Per Henrik Pedersen, DTI Energy (responsible for the project)

Michael Wedel Srensen, Confederation of Danish Industries

Morten Arnvig, AKB (Authorised Refrigeration Installers Association)

Tarjei Haaland, Greenpeace Denmark

Dorte Maimann, Danish Energy Agency

Lars Frederiksen, Danish Energy Agency

As mentioned in the aim of project, this will be performed in close co-operation with the Danish EPA and Danish industry.

Status report

A status report was written in the autumn of 1997. It was published in Danish and English (Working Report No. 101 and 102, 1997) and was also placed on the Internet via the Danish Ministry of Environment and Energy. This report is a revised and extended edition of the status report from 1997; data and knowledge about technology development have been updated. Specific suggestions to the Cleaner Technology projects have also been incorporated.

Organisation of work

State-of-the-art in 1995

The Danish EPA published three reports in English on alternative technologies in 1995. Thus, a comprehensive account on the state-of-the-art, as it appeared in 1995, is available within the refrigeration area, poly-urethane foam and substitution of halon for fire extinguishing.

This report is divided into different categories according to types of substances. Chapter 3 describes the consumption of HFC substances and their substitutes, chapter 4 refers to the consumption of PFC substances and chapter 5 deals with the consumption of SF6 and its possible alternatives.

During the project, DTI Energy has been in contact with a number of Danish enterprises and technological institutes to obtain knowledge. That is reflected in the descriptions of the individual areas of application and replacement possibilities.

The status report was prepared according to the comments from the steering committee and the steering committee’s member’s support bases, including the CFC group under the Confederation of Danish Industries. The comments were sent to DTI Energy and relevant factual comments were then included.

In addition, DTI Energy has received comments from the following persons: Jan Holmegrd Hansen, COWI, Erik Lyck, DMU (National Environmental Research Institute), Ole John Nielsen, Ris National Laboratory, Rolf Segerstrm, Electrolux, Stockholm and Alexander Pachai, AirCon A/S.

Lists of references on ammonia refrigeration systems, installed by Sabroe Refrigeration and Gram Refrigeration during recent years in Denmark, have also been received.

DTI Energy would like to thank everybody who has contributed to this report with comments and suggestions.

1998

In the final report all fields of application have been revised with regard to new information which e.g. has been obtained via renewed contact with relevant companies and from knowledge obtained about substitution possibilities from abroad.

Parallel with this report, DTI Energy has prepared a corresponding report for the Nordic Council of Ministers. It deals with more or less the same topics as the Danish report. However, some topics have been dealt with in greater detail such as e.g. consumption of SF6 in the production of magnesium, consumption of SF6 in connection with the production of power switches and emission of PFC substances in connection with aluminium production. These industrial fields are typical for other

Nordic countries.

On the other hand, the Danish report is more detailed about specifically Danish topics, e.g. production of refrigerators, cooling containers, district heating pipes, jointing foam and noise insulating windows.

Appendix B in this report has been prepared in co-operation with the Nordic project and will also form part of the Nordic report.

As it was possible to gain access to the status report on the Internet we have received inquiries from a number of foreign researchers. In particular, we would like to mention correspondence with Mr. Jochen Harnich from Massachusetts Institute of Technology who we have exchanged information with, in particular concerning consumption and emission of PFC substances and SF6.

# 3   Application of HFC substances and possible alternatives

HFC (HydroFluoroCarbons) is the name for various substances, which have been produced by placing a number of fluoride atoms on hydrocarbons. However, some hydrogen atoms will be left in the molecule. The most common HFC substances are:

| Substance | Chemical Formula | Boiling point (C) | GWP (100 yr) | Atmospheric life time (yr) |
| --- | --- | --- | --- | --- |
| HFC-23 | CHF3 | -82.1 | 11700 | 264 |
| HFC-32 | CH2F2 | -51.7 | 650 | 5.6 |
| HFC-125 | C2HF5 | -48.4 | 2800 | 32.6 |
| HFC-134a | CH2FCF3 | -26.5 | 1300 | 14.6 |
| HFC-143a | CF3CH3 | -47.5 | 3800 | 48.3 |
| HFC-152a | C2H4F2 | -24.2 | 140 | 1.5 |
| HFC-227ea | C3HF7 | -17.3 | 2900 | 36.5 |

Mixtures

The indication R-134a which is commonly used, means R for Refrigerant. The indication HFA-134a, which corresponds to HFC-134a, is also used. HFC substances are often used in refrigerant mixtures, which are provided with the R- 400 or the R-500 serial number. In annex A an overview of refrigerants and refrigerant mixtures is provided.

The HFC substances are used in Denmark mainly as refrigerants in refrigerators and as blowing agent of polyurethane foam. The HFC substances are also used for a number of minor purposes, for instance as propellant agent in special aerosol cans. Abroad, HFCs are used for special fire extinguishing purposes.

This chapter is divided in sections according to main consumption areas. In section 3.1 the refrigeration industry is discussed and the chapter is further divided, e.g. for domestic refrigerators and freezers, commercial refrigerators etc.

## 3.1	Refrigeration industry

15,000 employees

The refrigeration industry in Denmark is of significant importance and includes companies such as Danfoss, Sabroe, Gram, Vestfrost, Caravell, Elcold and Gramkow.

About 15,000 people are employed within the refrigeration industry, which has an annual turnover of more than 15 billion DKK. Thus, it is an industry of major importance to Danish economy and employment.

The refrigeration industry produces a large number of products covering a wide spectrum. From mass-produced refrigerators and freezers to industrial refrigeration plants, produced by Sabroe Refrigeration, one of the worlds leading manufacturers of such. In addition, various components for refrigeration plants produced by Danfoss, one of the worlds leading manufacturer of refrigeration components. Also minor refrigeration companies, assembling commercial refrigeration systems in supermarkets, could be mentioned.

This chapter is divided according to main products. Paragraph 3.1.1 describes domestic refrigerators and freezers. In this chapter both the consumption of HFC, used as refrigerant in refrigerators and the consumption of HFC as blowing agent of insulating foam in the cabinets are mentioned, as these areas of consumption are closely related.

### 3.1.1	Domestic refrigerators and freezers

1.5 million units/year

There are 6 Danish manufacturers of refrigerators and freezers, i.e. the companies of Vestfrost, Gram, Caravell, Derby, Frigor and Elcold. Annually, these companies produce app. 1.5 million units and most of them are exported. App. 1 million units are household refrigerators and almost half a million units are commercial refrigerators.

The annual sales in Denmark of domestic refrigerators and freezers has for years ranged between 250,000 and 300,000 units, among which a significant number of refrigerators are imported from Germany, Italy and Sweden in particular.

5000 employees

An estimated 5.000 people are employed within the production of refrigerators, freezers and components. Obviously, this industry is very important to Danish economy and employment.

Until 1993, domestic refrigerators and freezers were produced with CFC substances in the cooling circuit and in the insulation foam. App. 100 - 200 gram of CFC-12 was used in the cooling circuit and app. 500 gram of CFC-11 was used in the insulation foam.

In the following years the refrigeration industry went through a rather turbulent period due to a number of technologies being introduced as substitutes for CFC. At first, HCFC substitutes were used in replacement of CFC-11 in the insulating foam.

HFC-134a

Danfoss developed compressors that could use HFC-134a as refrigerant.

These technologies were introduced by Danish and foreign manufacturers of refrigerators in replacement of the CFC technology. From an environmental point of view the advantage was significant. The Danish manufacturers of refrigerators were some of the first deliverers of non-CFC refrigerators, which made them competitive on the European markets where restrictions on CFCs in refrigerators had been introduced. As a result of this, the production at Vestfrost in 1994 was more than 700,000 units.

After that time, demands also appeared to the phasing-out of HCFC substances.  Some companies introduced HFC-134a as blowing agent of the insulating foam. This was additional environmental progress compared to previous methods, as the refrigerators were now completely nondependent on any form of ozone depleting substances.

Potent greenhouse gases

The environmental organisations started to question the environmental impact of the HFC substances. Certainly, the HFCs are not depleting the

ozone layer, however they are potent greenhouse substances which will contribute to an increased greenhouse effect when released in the atmosphere. Thus, finding alternatives to the HFCs would be advantageous.

It should be mentioned that the CFC and the HCFC substances are potent greenhouse gases as well.

FORON

In 1992, Greenpeace Germany joined forces with the previous East German producer of refrigerators, FORON, and produced a refrigerator (called “Greenfreeze”) operating on a refrigerant mixture of propane and butane. The mixture had pressure and temperature conditions, corresponding to CFC-12, and the system was provided with a CFC-12 compressor. The entire system worked satisfactorily. By these means Greenpeace contributed effectively in breaking down a psychological barrier against the use of a flammable refrigerant.

Isobutane

Danfoss started up development of compressors running on the hydrocarbon isobutane, and German manufacturers of refrigerators, among others Bosch/Siemens, started to use these compressors. Shortly after, 35 types of refrigerators using isobutane as refrigerant were introduced by Electrolux. Thus, a comprehensive selection of refrigerators using isobutane as refrigerant was available.

Cyclopentane

At the same time it was discovered that the hydrocarbon cyclopentane could be used advantageously as blowing agent for polyurethane foam in refrigerators. This discovery was used in some German refrigerators and in many Electrolux factories. Both isobutane and cyclopentane have a very small direct impact on the greenhouse effect compared with the HFC substances. The GWP value of these hydrocarbons is app. 3, whereas HFC-134a accounts for a GWP value of 1300 (time frame = 100 years, GWP for CO2 = 1).

Germany

After this an avalanche started to slide, which in a few months forced the German refrigeration industry to convert to hydrocarbons. Also foreign manufacturers, who wanted to sell refrigerators in Germany, were forced to deliver refrigerators with hydrocarbon technology. This step was necessary, if they wanted to contribute to the selection of goods in warehouses and consumers magazines. More than 95% of the new refrigerators on the German market use hydrocarbons in the cooling system and as blowing agent for the insulating foam.

Fear of explosions

However, many people feared that an explosion accident might happen in some of the refrigerators due to the explosive mixture of hydrocarbons and air, which might appear in the cabinet. The danger that a spark from thermostat, door contact or lamp might ignite such explosive mixtures was imagined and debated.

This problem was solved by placing various potential spark-generating components outside the cabinet and to take preventive measures against any refrigerant leakage inside the cabinet.

At present, more than 20 million years of operation have been registered in Germany. According to available sources of information no accident has been registered so far.

Some people believe that the safety condition of the refrigerators has improved. Still, some people store lighter gas (for lighter refilling) in refrigerators. Unfortunately, this has caused explosion accidents in some old refrigerators where gas leaking from the gas dispenser was ignited by the thermostat or by the door contact.

Energy consumption

In addition, people were worried about the perspectives of increased electricity consumption after the new types of refrigerators had been introduced. This might have increased the contribution to the greenhouse effect caused by an increased CO2 emission from fossil fuels utilized at power plants. Also this anxiety proved non-relevant. The energy efficiency of the new hydrocarbon-based refrigerators is at least as good as the efficiency of the old system based on HFC substances.

Noiseless refrigerators

Refrigerators using isobutane as refrigerant are less noisy than refrigerators using HFC-134a, among others because of reduced pressure conditions in the compressor.

Another problem with HFC-134a is that it requires synthetic ester oil. It is very absorbent and it can be a problem that the oil sucks water from the air.

In Denmark the company Vestfrost quickly introduced hydrocarbon technology in the insulation foam and that i.a. took place with support from the Danish EPA.

In 1993-94, the Danish company A’ Gramkow in Snderborg developed a hydrocarbon charging station also supported by the Danish EPA. The company is now among the largest manufacturers of hydrocarbon refrigerant charging equipment for refrigerators in the world.

Danfoss is one of the worlds leading manufacturers of hydrocarbon compressors for refrigerators and freezers. App. half of the production, which takes place in Flensburg, Germany, is laid out for isobutane application.

EU’s Environmental Label

Hydrocarbon technology is making progress in Europe and certain developing countries, including Argentina and China. To achieve EU’s environmental label it became a demand in 1996 that refrigerators should not contain potent greenhouse gases in the refrigerant or the insulating foam. This means in practice that hydrocarbons are necessary to obtain the label.

In 1998, Vestfrost was awarded the EU environmental label for a combined refrigerator/freezer and as far as we know it is the first refrigerator that has received the EU environmental label.

Vestfrost

As far as we know, Vestfrost is the only Danish manufacturer who has converted to cyclopentane in the insulating foam. However, several other manufacturers have invested in equipment enabling the application of cyclopentane. For some of the other companies this means investments in factory rebuilding due to compulsory precautions against fire.

DTI Energy knows of another Danish manufacturer who has partly converted to cyclopentane.

The smaller Danish manufacturers use HFC as blowing agent for insulating foam. HFC is used because it still is less expensive than cyclopentane as it requires an increased amount of plastic when used. However, this aspect is being levelled by new plastics definitions.

| Tonnes | HCFC-22 | HCFC-141b | HCFC- 142b | HFC- 134a | HFC- 152a | R-404A |
| --- | --- | --- | --- | --- | --- | --- |
| Insulating foam | 0 | 0 | 7 | 264 | 0 |  |
| Refrigerant |  |  |  | 298 |  | 8 |

The consumption of HCFC and HFC substances (in tonnes) for the production of refrigerators and freezers in Denmark in 1997. The figures cover both domestic refrigeration units and commercial plug-in refrigerators and freezers. The figures are from ’Ozone depletion substances and certain greenhouse gases’, the Danish EPA, 1998.

Vestfrost is the only Danish manufacturer who can charge isobutane on all production lines.

271 types

In September 1996, Greenpeace Denmark carried out a survey on hydrocarbon refrigerators and discovered that there are more than 108 designs in the Danish market. Several refrigerators are imported from Germany, Sweden, Slovenia and Italy. Greenpeace is currently busy carrying out a new survey and the temporary results show that the number of hydrocarbon refrigerators has increased to app. 271. That corresponds to app. 41% of all models in the market.

It is DTI Energy’s impression that all Danish manufacturers realise that certain restrictions will be introduced in Europe as the Kyoto protocol has included HFC substances on the list of greenhouse gases that have to be reduced. The restrictions will comprise the future use of HFC substances and also that “it might become necessary to change to hydrocarbons”. However, Danish manufacturers still want to produce units with HFC substances for countries demanding these and in particular for the USA, where distribution of refrigerators charged with a flammable refrigerant is not possible for the time being.

Economic barriers

Non-HFC technology is available. In Denmark it is purely economic considerations that restrict the introduction of their use. These economic barriers mainly consist of investments in factory buildings, as rebuilding often will be necessary to secure fire-protecting areas in connection with the foaming process and charge of refrigerant. Furthermore, the investment in a hydrocarbon charging system and training of personnel will be necessary. Finally, approval of products together with accomplishment of laboratory tests for energy consumption measurements must be carried out.

New compressor techno-

logy

It should be mentioned that new technology is being introduced in compressors. Danfoss has developed a compressor range for domestic refrigerators. These operate on isobutane and have variable speeds, which generate considerable energy savings of 30 to 40%.

The energy savings are not achieved because of the refrigerant, but rather because of the possibility of optimising control of the device. The new compressors are included in the Danfoss product range and a sales increase is expected for the next years. The price is currently somewhat higher than the price of traditional compressors.

At DTU (the Technical University of Denmark) and Aalborg University tests on a similar compressor for refrigerators have been carried out together with Danfoss and Gram. Isobutane was used as test refrigerant and also in this case energy savings of 30 - 40% were measured.  In this case it was decisive to use isobutane as refrigerant, as application of HFC-134a would create a too large cooling capacity. This compressor has not yet been put into production.

Additionally, it should be mentioned that at present no hydrocarbon compressors applicable for direct current (12 V or 24 V) exist. HFC-134a is used as refrigerant in small refrigerators and freezers for trucks, yachts and other applications without main voltage. Development of direct current compressors for isobutane should be possible, but an investment from the compressor producer is necessary, which demands a market potential for these compressors.

Serum coolers

A number of serum coolers for application in e.g. India are produced in Denmark. Sales of these coolers are co-ordinated by WHO and UNICEF, who demand the use of HFC-134a as refrigerant. A considerable number of direct current compressors are used in these coolers, which are often run by solar cells (photovoltaric).

### 3.1.2	Commercial refrigerators and freezers

Ice-cream freezers and can coolers

The same companies which produce domestic refrigerators and freezers (Vestfrost, Gram, Caravell, Derby, Frigor and Elcold) account for a considerable production of commercial refrigerators and freezers. In particular, ice cream freezers and can coolers for retail shops are in question, but to a small extent refrigerators for hotels, restaurants, bakeries etc.

The production method of bottle coolers and ice cream freezers is almost the same as for domestic refrigerators. The insulating foam is produced in the same way as mentioned above. Vestfrost uses cyclopentan and the other parts use HFC.

Until now, no compressors for isobutane for commercial refrigerators have been available in the appropriate size.

New compressor

In co-operation with Vestfrost, Caravell and DTI Energy, Danfoss is developing a new compressor concept for isobutane as refrigerant and with variable speed. These compressors are adjustable to most commercial refrigeration units.

The first experiences show that the compressors function satisfactorily. This project is subsidised by means of the CO2 scheme under the Danish Energy Agency. 40 can coolers and 50 ice-cream freezers will be produced for testing in retail shops. In addition, a number of prototypes will be tested.

Great Britain

It should be mentioned that in Great Britain several units, using hydrocarbons as refrigerant, have been produced. Compressors for CFC-12 or HFC-134 have been used, in addition with a hydrocarbon mixture of propane/butane, having the same pressure/temperature conditions. Among others, Elstar has produced wine and beer coolers with hydrocarbons as refrigerant. This company has erected thousands of such coolers and solely uses hydrocarbons as refrigerant.

150 g

According to present standard specification the amount of flammable refrigerants is limited to 150 g. It is estimated that most commercial refrigerators and freezers will have a refrigerant charge smaller than this.

### 3.1.3	Commercial refrigeration systems

Commercial refrigeration systems are systems that e.g. are used for cooling purposes in supermarkets, speciality shops, hotels and restaurants and computer rooms. They can also be smaller refrigeration systems for industry.

Supermarkets

Typical commercial refrigeration systems are for instance used in supermarkets, where direct cooling has been used so far. The cooling compressors are placed in a machine room separated from the place of cooling.

Refrigerant is transmitted in long tubes into the retail shop, where evaporation takes place in the heat exchangers of refrigerators and freezers inside the shop. The refrigeration gas is sucked back to the compressors.

This principle occurs in numerous variations and sizes, from small bakery shops or butcher shops to computer offices, from hotels and restaurants to very large warehouses with more than 50 refrigeration systems.

In section 3.1.7 air conditioning systems are described, however it should be mentioned that there is no distinct difference between commercial refrigeration systems and air conditioning systems. Systems with several refrigeration locations, including air conditioning, are often seen.

Previously, CFC or HCFC based refrigerants like R-502, HCFC-22 and CFC-12 were used. In recent years many systems have been changed to HFC based refrigerants like HFC-134a or R-404a. New systems, built in recent years, are charged with HFC refrigerants as well.

In Denmark and abroad some new systems have been built recently. See more information later in this section.

| HCFC-22 | R-404a | Other HFCs |
| --- | --- | --- |
| 600 | 102 | 66 |

Consumption of HCFC and HFC substances in commercial systems in 1997 in tonnes (Ozone layer depleting substances and certain greenhouse gases, Danish EPA, 1998). It must be specified that consumption is classified as ‘Refrigerant (other areas)’ which is evaluated to be mainly commercial cooling and air-conditioning systems.

In addition, 54 tonnes of HFC-134a is used as ‘refrigerant (other areas)’. The 66 tonnes of ‘Other HFCs’ are 26 tonnes R-401A, 14 tonnes R-407C, 10 tonnes R-402A and 16 tonnes other HFCs.

Leakage

The commercial refrigeration area is the most heterogeneous one within the refrigeration industry. A large number of enterprises are involved in selling and installing refrigeration systems.  The refrigeration systems are composed of standard components provided for the purpose. Tubing is often quite extensive, earlier resulting in a significant rate of leakage per year, i.e. 20 -25% of the refrigerant charge.

AKB (Authorized Refrigeration Installers Association) has contributed considerably to quality improvement by securing that the systems remain tight. Nobody knows the exact leakage rate but AKB has prepared a policy about reducing the rate. However, there are limits to how tight the systems can become and that is especially the case for direct cooling in i.a. supermarkets.

On the other hand, if indirect cooling is applied, then refrigerant filling and leakage rates can be reduced drastically.

Great commercial value

There are many commercial refrigeration systems and therefore their commercial value is considerable. Still many old systems are operating on CFC refrigerants because a change to HFC based refrigerant would be a cost out of proportion with their age. Mainly, the newer refrigeration systems have been changed to HFC refrigerants.

It has been attempted to convert one particular system to propane, however the conclusion was that changing a CFC/HCFC or HFC system to propane is not realistic, as the required information for approval by the National Inspection of Labour in Denmark is seldom easily obtained.

KMO

Thus, it would be reasonable to continue operation with the existing systems but take appropriate precautions for leak proofness. When ready for scrapping, recovery of refrigerant is necessary for further treatment at the KMO (Danish refrigeration industry’s recovery and recycling scheme) for purification and reclamation or sending to destruction.

KMO is a voluntary arrangement within the refrigeration trade and has been supported by the Danish EPA.

Natural refrigerants

Natural refrigerants are substances that are already included in nature’s own cycle, for instance ammonia, hydrocarbons, CO2, water and air.

Systems for natural refrigerants to be used in supermarkets have been built in Denmark and abroad. Either ammonia or hydrocarbons are used as refrigerant. As these are not permitted in the shop itself, indirect cooling must be used, i.e. a secondary refrigerant (brine).

For many years, secondary refrigerants have been used in certain refrigeration systems, among others in water/glycol mixtures or water/saline mixtures. Recently, it has been mentioned that ice slurry or CO2 under high pressure could be used. Systems with indirect cooling are more expensive that systems with direct cooling as investments have to be made in an extra pump and a heat exchanger. In return, there will be less refrigerant leakage – down to app. 5% per year. Refrigerant charge is also much smaller than for corresponding direct systems.

In Sweden, there are demands for using indirect cooling. According to Svensk Kylnorm indirect cooling has to be applied if the refrigerant charge in the primary refrigerant system exceeds 30 kg. If the charged amount is between 10 and 30 kg the system has to be partly indirect which in practice means that the refrigeration of cold stores will be indirect while the refrigeration of freezers will be direct.

Ammonia refrigeration plant

The Danish Energy Agency and the Danish EPA have financially supported the construction of a new refrigeration system at Schou-Epa (now called Kvickly), which is the biggest supermarket in Roskilde near Copenhagen. An ammonia refrigeration plant is used, placed in a container on the roof of the building. A water/saline mixture is cooled in the ammonia refrigeration system, which is then pumped into the shop at two temperature levels to allow cooling or freezing.

The project is carried out by Sabroe + Sby in co-operation with DTI Energy. The system replaces more than 30 old CFC or HCFC-based refrigeration systems and energy savings amount to app. 35%.

However, energy savings in relation to a new, parallel coupled HFC refrigeration system would be insignificant and perhaps it would have a somewhat greater energy consumption.

Refrigeration systems, using ice slurry (a pumpable mixture of water, alcohol and ice, resembling thin sorbet ice) have been tested abroad. Ice slurry is a secondary refrigerant, which advantageously can be used for refrigeration purposes of up to 0C.

Some of these plants exist in Germany, Norway and England. However, this technology does not seem to be fully developed, as some teething problems have appeared.

Commercially accessible German and Canadian ice slurry generators are now on the market. The generator functions by means of ice that is generated inside a vertical or horizontal cylinder. Afterwards a mechanical scraper scrapes off the ice. The generators are rather expensive.

DTI Energy has developed a new principle for ice slurry generators without mechanical scrapers. Pumping the ice through a traditional heat exchanger with a special surface coating generates ice slurry. The generator has been developed with financial support from the Danish EPA, and at the moment tests are being carried out at DTI Energy in co-operation with Sabroe Refrigeration.

A new “Ice Slurry Centre” has been founded and various companies are involved in the project including Sabroe, Grundfos, tt-coil, Swep, Texaco, Georg Fischer, Hans Buch, Sunwell and Institute for Applied Chemistry, DTU. DTI Energy is involved in all development activities and carries out secretariat functions and administration of the centre.

The main objective of the centre is to develop and produce components for ice slurry. Knowledge and competence are transferred through the centre to products, thus ensuring functionality of the products and optimum interplay between them. The following products are to be developed: ice slurry generator, equipment for measuring ice concentration, pumps, pipe systems and valves, heat exchangers, storage equipment etc.

The centre is supported by the Danish Agency for Development of Industry and Trade and a user group is also connected, comprising FDB (the Danish Co-operative Union), the Danish Meat Research Institute and the Danish Fishermen’s Association.

Ice slurry is expected to become important to future refrigeration systems with indirect cooling in commercial refrigeration systems. Ice slurry will probably also be used for new refrigeration purposes such as direct contact freezing.

Pressurised CO2 can advantageously be used as refrigerant for freezing applications. Laboratory tests have been carried out in Denmark and systems exist abroad that use the same principle.

Small ammonia plants

In the Programme for Natural Refrigerants (included in the Cleaner Technology Programme) DTI Energy is currently carrying out 2 subprojects called “Introduction of ammonia in smaller refrigeration systems” and “Information to the Danish refrigeration trade concerning the use of ammonia in smaller refrigeration systems”.

The objective of the subprojects is to investigate and clarify problems in connection with the use of ammonia in small and smaller split-plants, to give advice and assign methods for plant design and to ensure that know-how is passed on to the refrigeration trade and realised in practice.

The projects include market research; description of fields of application and types of application; the preparation of safety measures, dimensioning rules, service and maintenance procedures; problem analyses regarding plant components, pipes and assembling methods; the development of laboratory equipment and tests with the same; construction and measurements carried out on demonstration plants, and reporting and participation in one-day conferences and seminars. The projects also include the formulation of a course programme and the preparation of information and instruction material.

The experimental work connected with the laboratory has become more extensive than planned. So far it has revealed that the problems against expectation not only have to do with the materials and assembly methods of the pipe system, but also in making the components operate satisfactorily with regard to refrigeration technology and acceptably with regard to energy consumption.

DTI Energy has carried out a demonstration project that was financially supported by the Danish Energy Agency. The objective of the project was to develop and demonstrate an ammonia based refrigeration plant for milk cooling at farms with reduced energy consumption and environmental impact.

In February 1998, the cooling system was put into operation at an ecological farm and it has functioned satisfactorily for 7 months. The complete installation comprises a system for cooling and storing milk as well as facilities for milk pre-cooling, drinking water heating, cooling accumulation and the utilisation of the condenser heat for preheating domestic water. Measurements have shown that the consumption of energy due to a low compressor efficiency was higher than expected, but lower than in connection with previous systems. Using ammonia and ice water as brine means that there will be no halogen-containing refrigerant leak detrimental to the environment. The plan is to change to an improved compressor. That will reduce energy consumption further.

Experience has been gained from the project that gives rise to believe that the concept can be developed to a competitive product programme. The project should be followed by new activities ensuring that the experience gained combined with innovation and new experiences from abroad are utilised for product development of future milk cooling systems in agriculture – with environmental refrigerants and low energy consumption.

Various projects are being planned including a project about solely using natural refrigerants at a large city hotel.

Sweden, hydrocarbons

In the course of the past couple of years, app. 75 new cold storage plants using hydrocarbons as refrigerants have been built in Sweden. They are based on a concept developed by Bonus Energi AB. An example is a new supermarket with a cooling system utilising hydrocarbons. The cooling capacity is 240 kW (for cooling) and 140 kW (for freezing). 7 semi-hermetic compressors are used. The refrigerants are a mixture of propane and ethane (Care 50") and the charge is 35 kg. As secondary refrigerants propylene glycol (for cooling) and CO2 (for freezing) are used. Bonus Energi AB was taken over by Sabroe A/S and the concept is now being marketed throughout Scandinavia, in Germany and the UK. Appendix E contains a reference list of the hydrocarbon cooling plants that have been erected by Bonus Energi AB. Linde AG in Germany has a similar concept.

It is now possible to purchase compressors for propane or propene. Bitzer compressors are used in the Bonus plants. In addition, AirCon A/S sells corresponding compressors from Dorin.

So far, no larger commercial cooling systems with hydrocarbons as refrigerants have been installed in Denmark, although several project reports have concluded that according to current Danish legislation there should be nothing against using hydrocarbons as refrigerant.

One of the reasons might be that in a discussion paper called “Without cooling most things get too hot” published by AKB in 1998, Mr. Flemming Jørgensen from Danfoss A/S warns against using hydrocarbons. FJ i.a. writes: ‘Within our trade in general we do not have enough know-ledge or experience and our education and not least supplementary education of the service sector must be supplemented with knowledge, rules, legislation and ordinary common sense when using and handling hydrocarbon-based refrigeration systems’.

Therefore, it is necessary to explain if actual problems exist – and if so, what the problems are – by means of planning and installation of a medium size commercial cold storage plant with propane.

A demonstration project should include planning, installation and operation of a plant with 100-150 kW cooling output and with propane charge greater than 7 kg. All relevant authorities ought to be involved. A measurement programme should be carried out to determine output, operating conditions and energy consumption. Afterwards instructions concerning how to carry out the programme and who has to be asked and to whom application should be sent etc. should be prepared.

A project should also include development of a basis for qualifying (supplementary) education for refrigeration fitters and service staff.

A project proposal concerning the above has been prepared.

It must be concluded that more experience is required by means of experimental tests with commercial refrigeration systems using indirect cooling. Especially, tests with ice slurry and CO2 as secondary refrigerants are necessary.

It is important that the safety aspects are fully considered and that regulations issued by the Danish National Labour Inspection are fully observed. In that connection it is important that light is thrown on the regulations needed.

The energy efficiency of new refrigeration systems is of great importance, and the energy consumption must not exceed the consumption of new HFC refrigeration systems.

It is important that the costs of refrigeration systems using brine systems (secondary refrigeration systems) are reduced to facilitate a wider use in the future.

It should be mentioned that the application of free cooling i.e. from outside air or harbour waters also is a possibility. Such measures might reduce energy consumption for refrigeration systems during some months of the year, as outside air e.g. can directly cool a room or harbour water can directly cool process water.

Evaluation of possibilities for using natural refrigerants within commercial refrigeration:

For future refrigeration plants the following can be stated:

The plants can be designed for ammonia as well as for hydrocarbons according to the safety measures required. In public premises it will normally be possible to use indirect cooling while indirect cooling can be used in many other cases.

- In the future large commercial refrigeration plants can be designed as ammonia or propane refrigeration plants using indirect cooling. Regarding fields of application large supermarkets could be mentioned.

- To some extent very small commercial refrigeration systems could be systems using hydrocarbons or ammonia with direct expansion. However, it is demanded that certain safety rules and firm procedures are issued/developed. Among others, the safety rules include a maximum amount of charge, e.g. 1.5 kg (for direct expansion). Suggested field of application is small refrigeration stores and refrigeration furniture in delicatessens, etc. Direct cooling can be used in connection with storage rooms with no public access.

-	The intermediate sized area is where the most important problems exist. Because of economic and safety reasons it might be a problem to build refrigeration systems using indirect cooling. Small everyday stores could be mentioned. As previously described, a number of development projects are presently in progress and they aim at developing new technology to narrow this rather grey zone area. Likewise, direct cooling can be used in connection with storage rooms with no public access.

### 3.1.4	Industrial refrigeration plants

Process cooling

Normally, industrial refrigeration plants are very large systems, which are used for process cooling within the foodstuff industry or in the chemical/biochemical industry. In Denmark, traditional ammonia refrigeration plants are used for such fields of application.

Ammonia plants

Almost all dairies, slaughterhouses and breweries make use of ammonia refrigeration plants. Sabroe Refrigeration is the leading manufacturer of industrial refrigeration plant, using mainly ammonia as refrigerant. Also Gram Refrigeration (York International) is known as supplier of industrial refrigeration systems using ammonia.

However, many industrial refrigeration plants use CFC, HCFC or HFC refrigerants, and in most cases this might have been ammonia refrigeration plants as well.

A tendency of using indirect system solutions prevails, for example in foodstuff industries, aiming to reduce refrigerant charge and to avoid ammonia outlet in areas of work etc. Hence, development of plants, using CO2 as refrigerant, will be required.

With financial support from the Danish Energy Agency, the company Sabroe Refrigeration and DTI Energy have developed a refrigeration plant, using solely water as refrigerant in the compression process. After production, the 2 MW demo plant was placed at Lego for cooling of casting machines producing plastic Lego bricks.

The efficiency of the plant is very high, and the energy consumption is app. 30% lower than for a newly optimised ammonia refrigeration plant. The plant has been fairly expensive to produce, and some years may pass before this technology is completely developed. It is expected that the Lego project will be followed by other projects involving the Danish Energy Agency.

### 3.1.5	Mobile refrigeration systems

Mobile refrigeration systems are refrigeration systems installed in cars, trains, aircraft, ships or integral reefer containers

Integral reefer containers

Mærsk Line

In Denmark the major field of application lies within integral reefer containers. The company Mrsk Line is the world leading carrier of refrigeration goods and has app. 40,000 cooling reefers in traffic on a global level.

Previously, integral reefer containers were quipped with a CFC-12 refrigeration system, and many old containers still use this equipment. Many new containers are changed to HFC-134a.

Since 1993, all new refrigeration systems have been installed with HFC-134a refrigeration plants. In Japan HCFC-22 is used for this purpose and in the USA substances like R- 404a and HFC-134a are used. Due to hard weather conditions at sea, the leakage rate of this type of refrigeration system is rather high.

Previously, CFC-11 was used in the insulating foam, but is now replaced by HCFC-141b.

Mrsk Container Industri A/S now produces integral reefer containers in Tinglev, Denmark, and production is considerable.

Thermo King Container Denmark A/S in Langeskov produces refrigeration systems to be installed in integral reefer containers.

Supported by the Danish EPA, DTI Energy in co-operation with industry has accomplished a survey aiming to examine the construction of future integral reefer containers.

CO2

The use of flammable refrigerants or ammonia for this purpose is problematic. At the moment, the range of natural refrigerants is thus limited to cover CO2 and possibly air as refrigerant.

In the course of the project the development of a prototype, testing CO2 as refrigerant, was suggested. Besides it is recommended to try using vacuum-insulation methods.

A Cleaner Technology project seems relevant for this area, and DTI Energy has in co-operation with industry formulated a project proposal concerning this matter.

A/C systems in cars

Previously, CFC-12 was used for this purpose, but in recent years HFC-134a has been used.

As Denmark has neither any car industry nor special hot climate conditions, no remarkable activities in connection with automotive air conditioning have been registered. However, the company AGramkow has produced charging equipment for the car industry. Still, in cars is an increasing area of application which might become standard equipment in the future.

CO2

In co-operation with important car manufacturers Danfoss has participated in an EU-project with the aim of developing a new type of system using CO2 as refrigerant. Danfoss has developed a new compressor for this purpose.

Hydrocarbons

It should be mentioned that in some countries hydrocarbons are used in car air conditioning systems. This is for example the case in Australia, where thousand of cars are using these refrigeration systems. Apparently, a hydrocarbon mixture is used together with conventional equipment, originally designed for CFC-12 or HFC-134a.

The possibility of fire and explosion accident occurrence in connection with application of hydrocarbons in car air conditioning systems has been debated. Hydrocarbons could be a natural choice, as several kg of hydrocarbons in the form of petrol, diesel oil and propane gas are already present in the car.

A/C systems in air planes

Cold air refrigeration system in air planes

For many years, a cold air refrigeration system was used for cooling passenger cabins in ordinary air planes. A simple joule process is used, where air is compressed and cooled by exchange with the surroundings. Afterwards, the air expanded in a turbine, whereby it turns cold. The energy efficiency of the process is not remarkably high, but it is used in planes because of the light weight of components.

A/C systems in trains

In Germany a project concerning a cold air refrigeration system for trains has been carried out. App. 60 units have been produced for ICE trains.

### 3.1.6	Heat pumps

The function of heat pumps is similar to that of refrigeration systems, as heat is tapped from a source (for instance fresh air, soil, stable air, process water, etc.). At higher temperatures this is removed to a heat carrier, for example central heating water.

The following three main types of heat pumps exist in Denmark: domestic heat pumps, stable heat pumps or industrial heat pumps.

Domestic heat pumps are used for space heating and for heating of water for domestic use. In Denmark, heat pumps are almost solely used in single family houses, but in Sweden and Norway a number of very large heat pumps are connected to collective heat supplies.

In Denmark, there are about 12 manufacturers of such heat pumps, and quite a number of Japanese units are imported.

Propane

Until now artificial refrigerants have been used, however the Danish producer Lodam has developed heat pumps using propane as refrigerant. In 1997, Lodam won a competition in Holland and therefore they have to deliver 400 heat pumps utilising propane to Dutch customers. This is a break-through for Danish, environmentally friendly heat pump technology. Lodam’s heat pump technology has been taken over by the Swedish company called Nibe. They will continue the production of heat pumps using propane.

Criteria have been accepted for the Nordic environment label concerning domestic heat pumps. According to these criteria no considerable greenhouse gases are allowed in the refrigerant of the heat pumps if they are to obtain the environmental label.

Like domestic heat pumps stable heat pumps are compact units utilising surplus heat from livestock. This heat is utilized for heating the house and/or for preheating of water for cleaning etc. in the stable. It is generally the same companies that install domestic heat pumps and stable heat pumps.

The Danish Energy Agency has financially supported a demonstration project on stable heat pumps.

Sabroe and Gram produce industrial heat pumps, and among other substances ammonia is used as refrigerant.

### 3.1.7	Air-conditioning systems

So far, no small air-conditioning systems for single family houses have been produced in Denmark, as our climate does not necessitate them in private houses. However, an increased marketing of air conditioning systems (often Japanese) in Denmark has been registered.

Previously, foreign manufacturers have used R-502 and CFC-12 and later HCFC-22 for this purpose and many foreign manufacturers are changing to HFC-based refrigerants, including HFC-134a and R-507C.

Propane

A foreign manufacturer (DeLonghi) has produced app. 60,000 air conditioning systems using propane as refrigerant.

IMI in the UK has sold plants with Care 50 (mixture of propane and butane). Models that can be mounted on walls and under ceilings are in question. The cooling output is between 2 and 10 kW.

It should be mentioned that a Danish manufacturer of dehumidifiers, Dantherm, uses HFC refrigerants.

Ammonia

The situation is different for large air conditioning systems in office buildings, hospitals etc. Here refrigeration systems (chillers) are installed for distributing cold water in the building. Air is cooled in heat exchangers by means of the cold water.

Various refrigeration systems are available for this purpose, and previously CFC-11 and other chemical refrigerants have been used. Ammonia is an excellent choice for this purpose and a system has been built/ installed at the main post office in Copenhagen. Furthermore, the system is equipped with a sea water heat exchange to utilise free cooling by means of cold harbour water for several months of the year, thus saving energy.

Sabroe

Appendix B includes a reference list of Sabroe’s ammonia refrigeration plants for chillers built in Denmark in the later years. Since 1990, 114 plants have been installed in hospitals, in large office buildings, within the process cooling industry, at Copenhagen Airport, within the foodstuff industries and at shopping centres.

Gram Refrigeration

Appendix C includes a similar reference list from Gram Refrigeration (York International) of ammonia chillers. 35 plants have been constructed since 1993, and these are installed in hospitals, in large office building, industries etc.

Similarly, it is possible to utilise propane in chillers for air-conditioning. Bonus Energi AB has erected app. 75 plants in Sweden. Appendix E contains a reference list of the plants.

Water vapour compression technology can also be used in connection with A/C. DTI Energy is involved in mechanical water vapour compression operated by electric energy and is also involved in thermal water vapour compression utilising hot waste water to produce cold water for  air-conditioning purposes. That takes place by means of ejector technology, where water is the working medium and also the refrigerant. Waste water is derived from decentralised power stations or industrial processes.

### 3.1.8	Cryogenic systems

The application of low temperature systems is relatively small. Refrigeration equipment is produced, which can cool laboratory tests and other equipment to very low temperatures.

Heto-Holten

Heto-Holten produces laboratory equipment, including equipment for freeze-drying and low temperature freezers (cryogenic systems) for hospitals etc.

Normally, the equipment consists of a two-step cascade refrigeration system, where the first step is an R-404a or an R-403B system. During the first step of the process, temperatures down to app. -50C are reached. During the second step hydrocarbons are used as refrigerants, either ethane (R-170) to app. -80 to -90C or ethene (R-1150) to app. 100 to - 120C.

Some foreign competitors use HFC-23 at the lowest step.

It should be possible to use propane during the first step. This would hardly influence the safety aspects, as flammable refrigerants are used already. However, compressors approved for propane are required and tests need to be carried out. There are indications that this is the case. According to the Danish agent of Dorin compressors they can be used for propane.

Possibly, other Danish companies produce cryogenic systems.

## 3.2	Polyurethane foam

The consumption of HCFC and HFC substances for production of polyurethane foam in Denmark in 1997 appears from the following table:

|  | HCFC-22 | HCFC-141b | HCFC-142b | HFC-134a | HFC-152a |
| --- | --- | --- | --- | --- | --- |
| Insulation in refrigerators | 0 | 0 | 7 | 264 | 0 |
| District hearing pipes | 0 | 0 | 0 | 0 | 0 |
| Other insulation material | 0 | 440 | 4 | 0 | 0 |
| Other rigid foam | 0 | 145 | 6 | 0 | 0 |
| Jointing foam | 0 | 0 | 0 | 44 | 5 |
| Flexible polyurethane foam | 0 | 0 | 0 | 40 | 10 |

Consumption of HCFC and HFC for production of polyurethane foam for various applications.

Consumption is stated in tonnes, and the figures have been taken from Cowi’s survey: Ozone depleting substances and certain greenhouse gases – 1997, Danish EPA, 1998.

As it appears quite an amount of HCFC is still used for foaming polyurethane foam. Especially HCFC-141b is in question. In the autumn of 1998, (according to trade sources) that lead to a shortage of the substance as several countries (including Denmark) has encountered a HCFC cap which has been laid down in the EU. Therefore, there is a limited amount to be used in the final part of 1998 and there has been a substantial price increase.

### 3.2.1	Insulating foam

As already mentioned in chapter 3.1.1, some amount of HCFC and HFC is used for insulation of refrigerators and freezers, and the available alternatives have already been described. Hence, this application will not be discussed in this chapter.

District heating pipes

Cyclopentane

More than half of the global production of district heating pipes takes place in Denmark by  ABB, I.C. Mller, Lgstr Rr, Tarco Energy and Dansk Rrfabrik (Star Pipes).

Previously, the consumption of CFC and HCFC was considerable. Thus, approximately 820 tonnes of CNC-11 was used in 1986. Today the insulating foam is blown by means of hydrocarbons, especially cyclopentane. In addition, some district heating pipes are produced with CO2.

World Bank funding

The Danish EPA has in co-operation with the industry obtained approval of the above mentioned type of district heating pipes for future projects by means of World Bank funding. This has contributed to a form of standardisation of pentane blown district heating pipes.

Mads Madsen from European District Heating Pipe s Association informs that Danish enterprises now deliver approximately 65% of the world production of district heating pipes. A small amount of this production takes place at subsidiary companies, e.g. in Poland.

About 1500 people are employed in district heating pipe factories in Denmark. In addition, some enterprises work with pipe laying and assembly of entire energy systems, etc. Enterprises, which are sub-contractors to district heating pipe enterprises, can also be mentioned. As can be seen, the importance to Danish economy and employment is considerable.

Insulating panels

At least two companies (D.C. System Insulation and Prepan, previously Dansystem) produce sandwich-insulating panels for cold store houses etc.

HCFC

Especially HCFC is used for this production, as some panels are also produced with CO2 to which a small amount of HFC had been added for export to Sweden, who has banned the use of HCFC panels. The exact amounts of HCFC are not known at the moment, but it is expected that a large amount of the HCFCs in the column other insulation foam will be used for this purpose.

In 1986, approximately 140 tonnes of CFC-11 were used for this purpose.

Alternatively, hydrocarbons, including cyclopentane, could be used. However, a large investment in production equipment is required. Certain foreign countries produce panels with hydrocarbons. In Finland e.g. Hurre Group Oy and Makroflex Oy produce sandwich-insulating panels by means of hydrocarbons.

Another alternative is to use CO2 (water blown) foam. Compared to other solutions, the insulation efficiency is poorer.

It is to be imagined that vacuum insulation is useable for this purpose in the future. A possibility could be production of sandwich-panels with rigid polyurethane foam with open cells. Afterwards, a vacuum pump will help to keep the pressure down in the insulation material. The foam itself is produced by blowing with CO2. Major efforts are required to develop this technology.

The greatest barrier against the introduction of hydrocarbons is the large investments required for rebuilding production equipment. Relatively small manufacturers are involved and relatively large investments will be required from them.

Integral reefer containers

HCFC substances

HCFC substances are used for production of reefer containers. The consumption of HCFC for this purpose in unknown, as it is included in the category other insulation foam in the Environmental Project No. 342. This is a relatively new production in Denmark.

The production could be changed to hydrocarbons (cyclopentane). However, some requirements were to be considered, including safety precautions for using cyclopentane as blowing agent. Furthermore, it should be considered that a possible reduction of insulation properties will change the construction of containers. Mærsk Container Industri A/S has stated that the transition to cyclopentane could lead to reduced insulating properties of up to 10%.

The greatest barrier against introduction of hydrocarbons is connected to the disadvantages caused by production stop, uncertainties about quality, security of working environment and the economical consequences hereof.

Vacuum insulation

Another possibility would be to use vacuum insulation, where rigid polyethane foam with open cells are used. A project has been worked out in co-operation with DTI Energy and industry concerning this matter. Comprehensive changes in construction and production are required if switching to this technology, and examinations and tests will be needed.

Other types of insulation foam

A number of minor manufacturerss of polyurethane foam use either HCFC or HFC for a number of purposes. It might be too expensive to invest in hydrocarbon technology, as large investments in fire protection are necessary.

CO2

Alternatively, foam blown by CO2 could be used, however the insulation conditions would decrease, compared with foam, blown by HCFC or HFC. In connection with certain applications the insulation properties are not decisive. That might be in cases where the construction implies that considerable heat bridges already exist or it can be in cases where there are no greater temperature differences.

In connection with the first item it can be mentioned that industrial gates with CO2 blown polyurethane foam are produced at Nassau Doors.

Another example is foaming of insulation material at Norfrig A/S who produces cooling boxes for lorries and semi-trailers. According to Mr. Chris Ungermand, Shell Kemi A/S, water blown foam is used. They have succeeded in developing a material with the same insulating properties as when HCFC-141b was previously used. That has happened by using glass fibre reinforced barriers on the sides. In that way diffusion of COs out of the foam and diffusion of air into the foam is avoided.

The company Tectrade A/S has also developed a new type of CO2 blown foam (often called water blown foam) where a finer cell structure leads to improved insulating properties.

Many of the smallest manufacturers of insulating foam have stopped producing the foam themselves. Instead they purchase “block foam” which is then cut to suit certain purposes. Often the foam is only a smaller part of a larger complex machine.

There is one Danish manufacturer of block foam and the company is called LM Skumplast. The company has replaced HCFC-141b with hydrocarbons (isopentane) for foaming. The plant has been designed by Tectrade A/S.

### 3.2.2	Jointing foam

Baxenden Scandinavia A/S

Baxenden Scandinavia A/S is manufacturer of aerosol cans with sealing foam and produce many different kinds. Previously, CFC or HCFC substances were used as propellant in these cans, but this has now been banned. In 1986 an amount between 575 and 800 tonnes of CFC and HCFC was used for this purpose.

Baxenden very soon introduced an alternative can, which used propane and butane as propellants. This system was introduced on the Scandinavian market, and since 1987 only systems operating on hydrocarbons have been used on this market.

Germany

The situation is different for other markets, including Germany. A maximum of 50 g flammable propellants may be stored in the cans, i.e. max. 50 g propane + butane.

HFC-134a

Thus, it is necessary to supply an amount of HFC-134a (a 700 ml can normally contains 100 to 175 g propellant).

This derives from an agreement, made by European manufacturers, but with the exception of Scandinavia. In other parts of the world hydrocarbons are used.

Only cans with pure hydrocarbon propellants are delivered to countries, used to work with this propellant, and where safety precautions concerning ventilation etc. are kept. Accidents with hydrocarbon based cans have occurred. This has happened in cases, where safety precautions have not been kept, and where use has taken place in small rooms, where fire has been ignited by a match or a lighter.

However, this danger also consists for cans using HFC substances, as this propellant, due to the content of hydrocarbon and HFC-152a, is flammable as well.

There are 35 manufacturers in the world, and competition is hard. Thus Baxenden cannot independently decide the technological trend, but may produce cans with HFC substances to other countries than Scandinavian.

Hydrocarbon is cheaper

Cans with pure hydrocarbon propellants are considerable cheaper than cans with HFC substances. The propellants have different qualities, thus a price comparison alone amongst the cans is not possible. The joint foam achieves different qualities depending on the propellant.

### 3.2.3	Flexible polyurethane foam

In Denmark there are two large manufacturers of flexible polyurethane foam, viz. Bdr. Foltmar and K. Balling Engelsen.

The main part of production is ’water’ blown, i.e. a small quantity of water is added during production. A chemical reaction between water and isocyanate will produce CO2, which is the actual blowing agent.

Some of the production has traditionally taken place using CFC-11 and later with HCFC substances as propellant. Especially soft and light quality items for the furniture industry should be mentioned.

HFC-134a and HFC-152a

In recent years a mixture of HFC-134a and HFC-152a has been used as propellant for this production.

Only CO2 blown foam is used in the other Nordic countries. An agreement has been made stating that foam with a density less than 23 kg/m3 should not be produced. Hence, no physical blowing agents are required.

Abroad a certain technology has been developed. Liquid CO2 is used for production of flexible polyurethane foam in these qualities, and some systems have been installed, amongst others in the USA and in Italy. The most important barrier against converting to this industry is investment in new machinery.

At least two manufacturers of the new technology should be mentioned, e.g. Canon (Italy) and Bayer (Germany).

Danish manufacturers of flexible polyurethane foam inform that there is also a barrier in connection with quality, as some quality problems with the new CO2 technology have appeared.

According to manufacturers of the above blowing technology equipment the quality of the new foam is satisfactory.

##### Methylene chloride	In certain countries (also in the EU) methylene chloride is used for production of flexible polyurethane foam. From a labour protection point of view this is not conceivable for application in Denmark.

## 3.3	Fire extinguishants

In connection with the global phase-out of Halon, a number of chemical substitutions have appeared, including one, which is based on HFC-227 (e.g. Great Lakes FM-200). These are marketed rather intensively in many countries of the world, and this has also been tried in Denmark.

Ban on HFCs

However, in Denmark the use of halogenated hydrocarbons for fire extinguishing is banned. The substances Halon-1301 and Halon-1211 were excepted from this, but they are now being phased-out parallel with the CFCs etc.

Inergen

Danish enterprises have developed impressive alternative technologies for fire extinguishing. Especially Inergen, which is developed by Dansk FireEater. It consists of inert gases, i.e. argon, nitrogen and some CO2. Inergen can be used for total room flooding systems in computer rooms, control rooms, power stations, engine rooms, etc.

Water mist

Ginge-Kerr Danmark A/S has a similar technology called Argonite, which consists of argon and nitrogen. In addition, this company has developed a water mist technology.

The technology of using inert gases for fire extinguishing purposes has become a remarkable success, also on an international level. Foreign multinational companies, such as Wormald, is marketing Inergen.

Other alternatives for chemical fire extinguishing have been developed, such as the use of CO2 or foam for fire extinguishing purposes in engine rooms on ships or cargo vessels, improved detectors combined with manually operated fire extinguishing etc. However, giving full details on this topic is beyond the scope of this report.

This entire area has been described in detail in a report published the Danish EPA in 1995: Environmental Report No. 312: Going towards Natural Fire Exhinguishants, Experience from Danish Industry.

## 3.4	Propellant in aerosol cans and foghorns

Ban on HFCs

The Aerosol Statutory Order, published by the Danish EPA, bans all application of HFC substances for use in aerosol cans.

The ban does not apply for medical aerosol cans or foghorns, as medical products are excluded as an exception and the publication does not regulate the contents in aerosol cans, where only gas is emitted from the can. However, a revision to include foghorns has been announced by the Danish Minister of Environment and Energy

Medical sprays

CFC-11 and CFC12 are still used as propellant in medical sprays, and especially in astma sprays. At the end of the 1980s the consumption of these products amounted to app. 29 tonnes of CFCs. The products are not manufactured in Denmark.

Alternative products have been available for many years, for instance self-inhalated astma powder. However, not all astma patients are able to inhalate themselves.

Astma sprays with HFC substances as propellant have been developed.

Foghorns

HFC-134a

Foghorns with HFC-134a as propellant can be bought. The horn is an aerosol can provided with a plastic horn, which is able to make a loud noise.

Is is estimated that most foghorns are used by the audience at football matches, however they are also used on sailing boats as alarm horns to warn other boats.

Non-HFC alternatives

Greenpeace Denmark has found non-HFC containing alternatives on the market. These alternatives are available in several types, where the one type uses isobutane as propellant. The other type uses compressed air, and re-loading is possible at petrol stations or by means of a hand pump.

Foghorns operating by means of an electric compressor are also available.  Finally, manually driven alarm horns, which can be blown up or may be activated by means of a rubber ball, are available.

## 3.5	Other fields of application

There is a small consumption of HFC in special cans for cooling electronic components during repair of electronic equipment. The flow of liquid HFC cools the component that the liquid drops come into contact with.

This method enables diagnosis of a defective component. The consumption is probably modest, app. 0.5 tonnes per year. According to Naturvårdsverket in Sweden CO2 is used for this purpose, and equipment is supplied by AGA.

DTI Energy has no knowledge of other fields of application for HFC substances in Denmark.

However, it should be mentioned that in South East Asia the so-called Pushn chill beer cans were planned to be marketed. These cans are chilled by means of direct evaporation of HFC-134a in the can, whereby the beer is chilled. This subject has been addressed by the press during the summer of 1997 and European ministers of environment have opposed this application of HFC substances.

The company behind the self-chilling can has recently announced that CO2 will be used as refrigerant instead of HFC-134.

# 4	Use of PFC substances

PFC means perfluorocarbons, i.e. substances that are formed with basis in simple hydrocarbons, where all hydrogen atoms are exchanged with fluoride atoms. These are substances like CF4, C2F6, C3F8, etc.

Very stable substances

As these substances are very stable, they have a very long atmospheric lifetime. At the same time they are very strong green house gases. However, only small amounts of these substances are used in Danish industry, and the main area of application lies within the refrigeration industry.

Abroad some PFC emission occurs in connection with aluminium production produced from aluminium oxide (alumina) by means of an electrolytic process. The PFC substances will only develop if a special effect, i.e. the anode effect, occurs. This means a rapid increase of the electric voltage during which certain PFC substances (CF4 and C2F6) are

produced. In Norway and Sweden considerable efforts in reducing development and emission of PFC substances have been made during recent years.

Abroad a considerable amount of the substance C6F14 is used within the electronic industry.

| Chemical formula | R-number | Boiling point (C) | GWP (100 yrs) | Atmospheric Life Time (yrs) |
| --- | --- | --- | --- | --- |
| CF4 | R-14 | -127.9 | 6500 | 50000 |
| C2F6 | R-116 | -78.2 | 9200 | 10000 |
| C3F8 | R-218 | -36.8 | 7000 | 2600 |
| C6F14 |  | +58 | 7400 | 3200 |

In 1990 the global emission of CF4 was app. 15,000 tonnes, which in 1995 decreased to app. 10,500 tonnes. In 1990 and in 1995 the global emission of C2F6 was app. 2,000 tonnes (personal information by Jochen Harnish, MIT).

## 4.1	PFC in refrigerant mixtures

According to a survey made by the Danish Environment Protection Agency app. 8 tonnes of C3F8 (R-218) were used in 1997 as refrigerant in a special mixture.

“Drop-in” substitute

The refrigerant is used as a drop-in substitute for CFC-12 in refrigeration plants. Consumption has been increased heavily since 1995 and 1996, with consumption of 1.5 and 3 tonnes respectively.

The refrigerant mixtures are known under various names, including Isceon 49 (R-413A), which consists of app. 88% HFC-134a, 9% C3F8 and 3% Isobutane.

New mixtures occur constantly, however the industry is most cautious about using refrigerant mixtures, as some uncertainty about the remaining mixture after leakage prevails. In general, transport of anymore types of refrigerants than necessary is undesirable.

| Trade name | R-number | Drop-in substitute for | Composition |
| --- | --- | --- | --- |
| Isceon 49 | R-413A | CFC-12 | 9% of C3F8, 88% of HFC-134a, 3% isobutane |
| Isceon 69L (Isceon 69S) | R-403B R-403A | R-502 | 39% of C3F8, 56% of HCFC-22, 5% propane |
| Suva 95 Forane 508A (Arcton TP5R3) | R-508B (R-508A) | R-13, R-503 (low temperatures) | 54% of C2F6 and 46% of HFC-23 |
| Arcton TP5R2 | R-509A |  | 56% of C3F8 and 44% of HCFC-22 |
|  | R-412A |  | 5% of C3F8, 70% of HCFC-22, 25% of HCFC-142b |

Table showing refrigerant mixtures, containing perfluorocarbons

Extension of Life Time

The mixtures may be conveniently used if extended lifetime of a CFC-based system is required and no recycled CFC refrigerant is available. The only reason for using these mixtures is their capability to extend the lifetime of old CFC based refrigeration systems. This application may be avoided by either converting the CFC refrigeration systems into HFC refrigerant or by maintaining tightness of system until scrapping. It is also possible to refill with used CFC from the KMO Recovery and Recycling Scheme.

## 4.2	Other applications of PFC substances

DTI Energy has not met other types of application in Denmark, but apparently small amounts are used in laboratories.

In Working Report No. 20, the Danish EPA 1996: Consumption of emissions of 8 fluoride and chloride hydrocarbons (Jan Holmegaard Hansen, Cowi), the following is mentioned:

One of the importers informs that the company has 2 products containing perflouro combinations on the import list. Both contain perflourohexane C6F14 as the main component, however, none of these products have been sold within the last year. The one product is an inactive liquid for use in the electronic industry, whilst the other product (an overactive product) is newly developed and thus never sold.

Fire extinguishant

It should be mentioned that attempts of selling a PFC substance as fire extinguishant in replacement for halon has been carried out abroad. This application of PFC is banned in Denmark, see section 3.3.

# 5   Consumption of SF6 and substitution possibilities

Danish consumption

SF6 (sulphurhexafluoride) is a heavy gas. According to the Environmental Project No. 342 (The Danish EPA, 1997) 13 tonnes of SF6 was used by Danish industry in 1997. The corresponding figures from 1992, 1993, 1994, 1995 and 1996 are 15, 17, 21, 17 and 11 tonnes, respectively.

Glass industry (noise insulated windows) is the far biggest area of consumption. In second place metal works and power plants can be mentioned.

Some very small areas of application can be mentioned. DTI Energy only knows the application of tracer gas and blowing of car tyres. Apparently, there are some other applications, for instance laboratory use.

| Chemical formula | R-number | Boiling point (C) | GWP (1 (100 yrs) | Atmospheric Life time (yrs) |
| --- | --- | --- | --- | --- |
| SF6 | R-7146 | -63,8 | 23900 | 3200 |

Global consumption

The global consumption of SF6 is app. 7,500 tonnes per year, the amount of which is still increasing. The largest amount (app. 6,000 tonnes per year) is used as dielectric in high voltage installations in e.g. S.E. Asia, where especially the rapid growth of the electricity supply uses large amounts of SF6. In the old industrialised countries this extension was carried out some years ago, and the consumption of SF6 for electrical installations is relatively small because of recycling or re-use.

The second-largest source of consumption on a global scale is for magnesium production (app. 500 tonnes per year). Other global fields of consumption include degassing of aluminium, cleaning of electronic components and blowing of car tyres.

## 5.1	Noise-reducing double glazed windows

SF6 (sulphurhexafluoride) is gaseous at normal temperatures and atmospheric pressures. SF6 is used in some noise-reduced double glazed windows, where SF6 in an argon mixture fills the space between the panes of glass. The purpose is to absorb acoustic waves and thus secure against noise from the outside.

7.2 tonnes of SF6

According to the Danish Environment Protection Agency an amount of 7.2 tonnes of SF6 was used in 1997 for this purpose. This examination has mainly been prepared according to information from suppliers and importers of SF6. The consumption of SF6 for this purpose is declining, and in 1995 and 1996 the amount used was 13.5 and 9.4 tonnes, respectively.

Some of the production is sold in Denmark. There are app. 30 producers of this type of noise-insulated double glazed windows in Denmark.

According to a survey made by the Danish Environment Protection Agency a direct emission of SF6 occurs during charging of the windows. This loss varies between 10 and 20% depending on the equipment and the procedures used. Previously, the amount of emission was much bigger.

Initially, SF6 is accumulated in the windows, however, when the windows puncture, the substance will leak out into the atmosphere.

Emission

As no collection or recovery arrangements exist, which would be difficult whatsoever, the entire amount of SF6 will probably end up in the atmosphere. As this type of window has been produced for some years (15-20 years), it is expected that some emission from old windows with SF6 will occur in connection with puncture or scrapping of the windows. If we assume that the lifetime for these windows is 20 years, we are about to reach the point where the actual emission corresponds with the raw material consumption.

DTI Energy has consulted Peter Vestergaard from DTI Building Technology and manufacturer representatives. The information received hereby was that:

- The environmental hazards related to the use of SF6 surprised everybody. They did not think that the end-users (e.g. the city refurbishing corporations) were aware of this matter

- The consumption of was considered surprisingly high

- SF6 creates slightly poorer heat insulating properties compared to standard glasses

- Noise insulated windows are always a combination of other factors like glass in different thickness and possibly laminated

- SF6 only contributes to a minor degree to noise reduction

Cleaner Technology

Cleaner Technology efforts seem relevant in this area, and the environmental effect may be considerable if a positive result of this project is achieved.

DTI Energy has contacted Delta Acoustics and Vibration with the purpose of formulating a project within the area.

A project proposal has been prepared, in which the initial part of the project (subproject 1) contains a more precise description of the production of noise-insulated windows, e.g. type of window, number and application concerning the extent of traffic noise, expected life time etc. Laboratory measurements on 8-10 windows with SF6 will be carried out together with parallel measurements on similar windows not containing SF6. Thus, the aim of subproject 1 is to demonstrate the importance of using SF6 as a noise-insulating medium, where after targets for the following part of the project (subproject 2) will be decided upon. Finally, new concepts of windows not containing SF6 will be prepared in co-operation with manufacturers.

## 5.2	Protective gases in light-metal foundries

According to the Danish EPA the consumption in 1997 of SF6 used as protective gas for light metal casting, was 0.6 tonnes. The consumption in 1995 and 1996 was 1.5 and 0.4 tonnes.

Magnesium

The production takes place at the company Metallic A/S. Here SF6 is used in a mixture of other gases (CO2 and atmospheric air) to protect liquid magnesium from igniting, when casting the metal for machinery parts. Liquid magnesium is highly flammable and will ignite when exposed to air.

The same method is used in other countries. A search on the Internet reveals that a number of different magnesium casting machines exists, all protected with SF6 systems. SF6 will be released from this source to the environment.

Metallic A/S also casts goods in aluminium, zinc and brass, but the use of SF6 exclusively takes place when casting magnesium.

Increased consumption

According to Lars Feldager Hansen, Metallic A/S, magnesium is a very light and strong metal. Consequently, the use of magnesium parts is increasing in the car industry.

Metallic A/S is currently rebuilding their factory in order to terminate the use of SF6.  Application of SO2 in closed machinery parts will be introduced instead. Partial implementation of this technology has already been carried out and full implementation is expected during the next year. The new technology has been introduced in co-operation with Norsk Hydro.

Aluminium production

Degassing liquid aluminium

According to Preben Norgaard Hansen, DISA A/S, SF6 is used for degassing liquid aluminium before casting. Previously, chlorine-containing gases were used for this purpose, however due to the working environment this caused problems.

SF6 is introduced into the liquid metal in small bubbles where gas, including hydrogen, diffuses into the bubbles, which rise to the surface to be released in the atmosphere.

On a global level app. 20 Disamatic automatic casting machines for aluminium production exist. This market is growing steadily, as the use of aluminium for car parts is increasing.

DISA has previously tested this technology at their test foundry in Denmark, but is presently not using SF6 for this purpose. Per Norgaard Hansen is not aware of the use of SF6 for aluminium casting in Denmark.

## 5.3	Insulating gas in electric power switches

Dielectric value

SF6 has a remarkable dielectric value. Because of this, the substance is used as insulating gas in certain high voltage installations. In principle, there are two different fields of application:

-	as arc-extinguisher in switches

-	as insulator in compact distribution systems

According to figures registered by the Danish EPA, the consumption of new SF6 for these purposes was app. 1.4 tonnes in 1995, 1 tonne in 1996 and in 1997 the consumption was app. 4.2 tonnes. Probably, the installed amount is much higher, but the emission is limited because the gas is kept in closed equipment and because the gas is collected and recycled when maintaining or disassembling the equipment. Thus emission only occurs by accident or unexpected leakages.

Electric arc

According to Henrik Weldingh, DEFU (Research Institute of Danish Electric Utilities), an electric arc will be formed when switching off the power, and temperatures may reach extreme values (10,000 - 100,000 K). A substance is needed for breaking the electric arc by rapid and efficient cooling, so that power cut off is completed by the time the current reaches the zero point of the AC sine wave.

Several possibilities prevail, such as:

-	The electric arc is blown away by means of highly pressurised air from a vessel. This technology is old and is still used in some systems. A disadvantage is that the release of the compressed air makes a loud noise resembling an explosion

-	Using oil, by which hydrogen is formed. This technology implies a certain risk of explosion and has been abandoned

-	Switching off the current in a closed vessel containing SF6. This method works satisfactorily

-	Switching off the current in a vacuum chamber. This technology also works satisfactorily in the range up to 20 kV.

No Danish producers of this equipment exist. However, multinational companies like ABB, Siemens, Group Schneider etc. produce this type of equipment.

Non-SF6 circuit switch

In Denmark about 600 transformer stations in the 10-20 kV range exist, which are either equipped with SF6 or vacuum switches. Prices are similar and competition is hard amongst the producers. Thus non-SF6 circuit switches for the 10-20 kV transformer stations are available. However, space related problems may arise when changing to this type, and rebuilding of the entire station may be necessary.

Non-SF6 solutions

In addition, about 60,000 of 10 kW/400 V sub-stations exist. In this case the equipment may be based on SF6 both as switching and insulating agent, but other non-SF6 solutions are available. Because of the large number of sub-stations, parameters like reliability, maintenance and small physical size play a decisive role.

In the high voltage range from 60 kV and up there are no alternatives.

According to Henrik Weldingh, DEFU, new technology is not in sight. New semiconductors may be marketed in the future, but a technological break-through is required, as efficiency is too low with the known technology.

The other application within the electrical area is as insulating gas in compact transmission cables. As an example high voltage cables of 400 kV, from the generator and out of the power plant, are placed in pipes (for example in 20 m), filled with SF6. This prevents flashover to the pipe and thus short-circuiting power cables. Alternatively, the distance between the cables could be increased, allowing atmospheric air to become the insulating agent.

As no Danish manufacturers of this type of equipment exist, the initiation of development projects seems pointless within this area.

If application of a technology, not containing any strong green house gases is wanted, installation of non-SF6 switches in the 10 kV system is possible.

## 5.4	Tracer gas and other laboratory purposes

According to the Danish EPA, the consumption of SF6 by various research institutes is app. 0.6 tonnes per year.

Tracer gas

DMU (the National Environmental Research Institute) uses a small amount of SF6 as tracer gas for tests of dispersal in the atmosphere. The purpose of these experiments is to test mathematical models for dispersal in the atmosphere. This kind of tests makes among others the foundation for standards of chimney heights, etc. Only small amounts are used, varying according to actual projects. According to Erik Lyck, DMU, an amount of 6 kg was used in 1995, in 1996 no amount was used, and in 1997 less than 100 g was used. In 1998 no application has taken place so far.

The application of SF6 as tracer gas is due to a number of special qualities of the substance, which makes it hard to replace. Among others, it is precisely and specifically detectable in very low concentrations and the concentration in atmosphere is very low. Foreign tests have been made with a PFC substance, however this causes environmental problems as well.

Background level

Erik Lyck estimates that there are no useable alternatives, however the amount used for tests has to be limited and controlled. The tracing equipment of DMU is that sensitive that the background level for SF6 is measurable. Erik Lyck has written an article about this subject.

Ventilation tests

In Denmark, app. 5 laboratories are performing ventilation tests. Small amounts of SF6 are used as tracer gas for indoor tests. The measurements are used for estimation of pollution dispersal, leakage from heat exchangers and estimation of short circuit between the airstreams, etc.

Christian Drivsholm, DTI Energy in Taastrup informs that 2 kg per year are used for these tests. Laughing gas (N2O) may be be used as well, however this is slightly problematic because of toxicity.

## 5.5	Car tyres

According to the survey by the Danish EPA no consumption of SF6 for car tyres is registered. According to various sources of information large amounts of SF6 are used in Germany (in the order of 100 tonnes per year) for the blowing of car tyres. Consequently, DTI Energy has tried to elucidate this use.

According to conversation with Rudolf Nielsen, DTI Energy, Torben Skovgaard, The Danish Tyre Safety Council and Jan Steen Hansen, Continental, the situation is as follows:

“Conti Air Safe”

A German company named Messer Griesheim (near Hamburg) tried to sell a system, called Conti Air Safe to Continental, Denmark. The system was tested in 1990, but has not been introduced.

The sales argument was that the SF6 molecules, which are rather big, would be mixed with air in the car tyre, diffuse into the tire material and prevent/reduce diffusion of air out of the car tyre.

According to above mentioned persons no SF6 is used for this purpose in Denmark.

## 5.6	Other possible applications of SF6

At present DTI Energy has no knowledge of other applications of SF6 in Danish industry than the above mentioned.

Nike sports shoes

However, DTI Energy knows that SF6 are used in the soles of Nike sports shoes. According to a letter from Sarah Severn, Director for Nike Environmental Action Team to Greenpeace Denmark (dated September 12, 1997), the consumption of SF6 from April 1, 1996 to March 31, 1997 was 288 tonnes. The substance is used in Nikes Air models, and the entire production of these soles is located in the USA.

At the same time Nike announced that a phase-out over three years of the use of SF6 is initiated and not later than year 2001 SF6 will be replaced with nitrogen.

According to the recent letter of August 17. 1998, from Sarah Severn Nike, the consumption of SF6 in 1997 was app. 276 tonnes and the consumption in 1998 is estimated to be app. 164 tonnes. This corresponds with a 40 % reduction.

Nike also states, that the consumers can not clearly differentiate between shoes produced with SF6 and with nitrogen.

# 6	Evaluations and recommendations

A number of activities have been initiated for the development of HFC substitutes. Many results have been achieved and satisfactory results are expected of the many current projects.

As mentioned in chapter 3, a number of projects are going on, i.e.:

Danish EPA

Danish EPA: Programme for Natural Refrigerants:

- Development of small ammonia systems, including new assembling methods

- Development of ice slurry generator

- Integral reefer containers with natural refrigerants (preliminary study). This project has been accomplished and a final project proposal has been prepared.

Danish Energy Agency

The Danish Energy Agency has supported the following projects in progress:

- Supermarket refrigeration system using ammonia and indirect cooling

- Water vapour compression system

- Energy saving commercial refrigerators and freezers using isobutane

- Cooling with natural refrigerants within the hotel branch

- Milk cooling system using ammonia for use at a farm.

Noise reducing windows

The initiation of a Cleaner Technology project on substitution of SF6 in noise reducing windows is recommended. This should be carried out in co-operation with for instance manufacturers.

Integral reefer container

The initiation of a Cleaner Technology project in substitution of potent green house gases in integral reefer containers is recommended. This should be carried out in close co-operation with relevant industry. The project should consist of two parts, where the first part is development and testing of a new cooling system, using CO2 as refrigerant. The second of part is development and testing of new insulating concepts. One or two containers should be produced and tested in practice.

Commercial cooling

Further efforts with commercial refrigeration are recommended. For instance ammonia or hydrocarbons for direct or indirect cooling can be used. Construction and testing of a demo plant has to be carried out. In addition, a parallel education programme for refrigeration fitters must be prepared. This project will be made in co-operation with the relevant authorities.

Internet

The establishment of a homepage on the Internet is recommended in order to allow world-wide distribution of Danish results. Links to relevant homepages should be established on this homepage.

Later on projects on other subjects involving potent green house gases can be initiated, in case of promising concepts.

Highest priority of projects in areas where Danish production and know-how already prevail is recommended. By means of this, an optimum synergistic effect is assured to secure an efficient development of new products without green house gases.

- Project proposals for the Cleaner Technology programme

On the basis of the evaluations and the recommendations in chapter 6 the following lists of proposals for Cleaner Technology projects are made, whilst the proposals are categorised into two priorities:

At short sight the following projects should have highest priority in the Cleaner Technology programme:

- 		Development of noise insulating windows without SF6

- 		Integral reefer containers with CO2 refrigeration system and new insulation

-		Commercial cooling systems with hydrocarbons

- Information on natural refrigerants and other substitutes for HFCs, PFCs and SF6, including creation of a homepage showing the latest results, reports, etc.

On a slightly longer sight the following areas should be considered:

-	Insulating panels without HFC or HCFC

-	Flexible polyurethane foam without HFC

-	Blowing of other insulating foam without HFC

-	D.C.-compressor for refrigerators (for isobutane)

-	Low temperature cooling systems with natural refrigerant

# 8	Literature

In the report the following literature has been used:

- Environmental Report No. 342: Ozone depleting substances and certain green house gases – 1995. Prepared by Jan Holmegaard Hansen, COWI. Danish EPA 1997.

- Working report No. 98, 1997: Ozone depleting substances and certain green house gases – 1996. Prepared by Jan Holmegaard Hansen, COWI. Danish EPA 1997.

- Ozone depleting substances and certain green house gases – 1997.  Environmental project to be published in 1998 by the Danish EPA. Prepared by Jan Holmegaard Hansen and Thomas Sander Poulsen, COWI.

- Working report Nr. 20: Consumption and emission of 8 fluorine and chlorine hydrocarbons. Danish EPA 1996.

- Svend Auken, Danish Minister for the Environment and Energy, Official Opening of the Conference, Application for Natural Refrigerants, Aarhus, Denmark, 3. – 6. September 1996. International Institute of Refrigeration, Paris.

- List of undesireable substances. Review No. 7, 1998, Danish EPA, 1998.

- Environmental Project No. 300: Polyurethane Foam without Ozone Depleting Substances; Experience from Danish industry. Danish EPA 1995.

- Environmental Project No. 301: Going towards Natural Refrigerants; Experience from Danish industry. Danish EPA 1995.

- Environmental Project No. 312: Going towards Natural Fire extinguishant; Experience from Danish industry.

- Greenfreeze – refrigerator types available on the Danish market, Status March 1998. A user’s guide prepared by Greenpeace (under revision). For further information see www.greenpeace.org/~dk.

- Scandinavian Refrigeration (ScanRef) 4/1997. Article about a Swedish supermarket refrigeration system using hydrocarbons as refrigerant. (In Swedish).

- Scandinavian Refrigeration (ScanRef) 3/1998. Hvad skal vi med TEWI? Bjørn Grødem. (In Norwegian).

- Hans Haukås, Reduksjon i forbruket av HFK, tiltak og kostnadar, Rapport 97:32 Statens Forurensningstilsyn. (In Norwegian).

- Uden køling bliver det meste for varmt. Discussion on the use of refrigerants in retailing, industry and at the end-user. Prepared by AKB (Authorised Refrigeration Installers Association), 1998. (In Danish)

- Kathryn Ellerton, Allied Signal Inc: Recent Developments and the Outlook for Global Sulphur Hexafluoride, International Magnesium Association Fifty-four, Toronto, June 1997.

- Letter from Sarah Severn, Director, NIKE Environmental Action Team to Tarjei Haaland, Greenpeace Denmark, dated September 12, 1997.

- Environmental Report, Norsk Hydro, 1997.

- Letter from Sarah Severn, Director, NIKE Environmental Action Team to Tarjei Haaland, Greenpeace Denmark. Dated August 17, 1998.

- Possibilities in reducing consumption and emission of potent green house gases (HFCs, PFCs and SF6). Project for the Nordic Council of Ministers. Preliminary report dated October 1998.

- Various brochures from Danish and foreign enterprises.

# Appendix A: List over refrigerants and refrigerant mixtures

In the below table the most common refrigerants, consisting of single substances, are stated:

| Substance | R-number | Chemical formula | ODP-value | GWP-value (100 yrs) |
| --- | --- | --- | --- | --- |
| Halon-1301 | R-13B1 | CBrF3 | 10 | 5.600 |
| CFC-11 | R-11 | CFCl3 | 1.0 | 4.000 |
| CFC-12 | R-12 | CF2Cl2 | 1.0 | 8.500 |
| CFC-115 | R-115 | CClF2CF3 | 0.6 | 9.300 |
| HCFC-22 | R-22 | CHF2Cl | 0.055 | 1.700 |
| HCFC-124 | R-124 | CF3CHClF | 0.03 | 480 |
| HCFC-142b | R-142b | C2H3F2Cl | 0.065 | 2.000 |
| HFC-23 | R-23 | CHF3 | 0 | 11.700 |
| HFC-32 | R-32 | CH2F2 | 0 | 650 |
| HFC-125 | R-125 | C2HF5 | 0 | 2.800 |
| HFC-134a | R-134a | CH2FCF3 | 0 | 1.300 |
| HFC-143a | R-143a | CF3CH3 | 0 | 3.800 |
| HFC-152a | R-152a | C2H4F2 | 0 | 140 |
| HFC-227ea | R-227ea | C3HF7 | 0 | 2.900 |
| PFC-14 | R-14 | CF4 | 0 | 6.500 |
| PFC-116 | R-116 | C2F6 | 0 | 9.200 |
| PFC-218 | R-218 | C3F8 | 0 | 7.000 |
| Isobutane (HC-600a) | R-600a | CH(CH3)3 | 0 | 3 |
| Propane (HC-290) | R-290 | C3H8 | 0 | 3 |
| Ethane (HC-170) | R-170 | C2H6 | 0 | 3 |
| Ethene (Ethylene) | R-1150 | CH2CH2 | 0 | 3 |
| Propylene (HC-1270) | R-1270 | C3H6 | 0 | 3 |
| Ammonia | R-717 | NH3 | 0 | 0 |
| Carbondioxide | R-744 | CO2 | 0 | 1 |
| Air | R-729 | - | 0 | 0 |
| Water | R-718 | H2O | 0 | 0 |

From below mentioned table various refrigeration mixtures in the 400-serie (zeotropic mixtures) appear. Calculation of the ODP and GWP values is possible according to the values in the table for single substances, as the ratio of mixture according to single substances is weighted.

| R-No. | Substances | GWP-value (100 yrs) | Concentration in weight-% |
| --- | --- | --- | --- |
| R-401A | HCFC-22/HFC-152a/HCFC-124 | 1082 | 53/13/34 |
| R-402A | HCFC-22/HFC-125/HC-290 | 2326 | 38/60/2 |
| R-403A | HCFC-22/PFC-218/HC-290 | 2675 | 75/20/5 |
| R-403B | HCFC-22/PFC-218/HC-290 | 3682 | 56/39/5 |
| R-404A | HFC-143a/HFC-125/HFC-134a | 3260 | 52/44/4 |
| R-406A | HCFC-22/HC-600a/HCFC-142b | 1755 | 55/4/41 |
| R-407C | HFC-32/HFC-125/HFC-134a | 1526 | 23/25/52 |
| R-408A | HCFC-22/HFC-143a/HFC-125 | 2743 | 47/46/7 |
| R-409A | HCFC-22/HCFC-142b/HCFC-124 | 1440 | 60/15/25 |
| R-410A | HFC-32/HFC-125 | 1725 | 50/50 |
| R-412A | HCFC-22/HCFC-142b/PFC-218 | 2040 | 70/25/5 |
| R-413A | HFC-134a/PFC-218/HC-600a | 1774 | 88/9/3 |
| R-414A | HCFC-22/HCFC-124/HCFC-142b/HC-600a | 1329 | 51/28.8/16.5/4 |
| R-415A | HCFC-22/HFC-23/HFC-152a | 1966 | 80/5/15 |

Refrigeration mixtures in the 500 serie (azeotropic mixtures) appear from the following table:

| R-No. | Substances | GWP-value (100 yrs) | Concentration in weight-% |
| --- | --- | --- | --- |
| R-502 | CFC-115/HCFC-22 | 5576 | 51/49 |
| R-507 | HFC-143a/HFC-125 | 3300 | 50/50 |
| R-508A | HFC-23/PFC-116 | 10175 | 39/61 |
| R-508B | HFC-23/PFC-116 | 10350 | 46/54 |
| R-509A | HCFC-22/PFC-218 | 4668 | 44/56 |

# Appendix B: Commercial refrigeration systems

The commercial refrigeration systems installed in retail stores, supermarkets, restaurants, computer centres etc. account for the most important economic area within the refrigeration industry. In addition, the widest range of applications lies within this area. On this background various conditions like prices, energy consumption, refrigerant leakage and the TEWI value (Total Equivalent Warming Impact) will be elucidated in this appendix.

In chapter B.1 a price comparison between liquid chillers using R-404A, hydrocarbons and ammonia is made, whereas conditions like energy consumption, refrigerant leakage and the TEWI value for supermarkets systems are addressed in chapter B.2. In chapter B.3 detailed price differences between a traditional refrigeration system and a similar refrigeration system using hydrocarbon refrigerant are shown.

B1. Comparison of prices between ammonia, hydrocarbon and HFC refrigeration systems (liquid chillers)

The comparison will be based on liquid coolers (chillers) and on this background price differences and the reason for such will be analysed. An estimate of how prices are expected to develop in the future is given.

Today HFC and ammonia refrigeration systems are produced in large quantities. Basically, the HFC refrigeration systems use the same technology as CFC and HCFC refrigeration systems, and ammonia refrigeration systems have been produced for more than 100 years. Recently, ammonia has been replaced by artificial refrigerants, however application of ammonia is rapidly in progress within the field of large liquid coolers, air conditioning etc.

Compared to this, the use of hydrocarbons is relatively new within the area of commercial refrigeration systems. Some of these are produced in Sweden and Germany, where quite a number of refrigeration systems operating on propane or propene has been installed. These systems are produced in small quantities and compared to HFC refrigeration systems prices continue to be relatively high. A rapid improvement of competitiveness could be possible.

###### Haukås

A report for SFT, Norway (Report 97:32, SFT) has been prepared by Hans T. Haukås. This report includes prices on various types of refrigeration systems.

According to Haukås the following prices for systems over 10 kW are to be taken into consideration:

-	a 12.5% price increase for refrigeration systems using HFC-134a compared to systems using R-404 or R-507

-	a 10-40% price increase for liquid cooling aggregates using ammonia or hydrocarbons compared to systems using R-404A or R-507

-	application of ammonia or hydrocarbon requires a certain extra charge for machine room safety

According to Haukås, the figures should be regarded as guides and some examples deviate on both sides of the scale. As far as large refrigeration systems are concerned, application of ammonia will be directly competitive. No investigation has been carried out as far as application of hydrocarbons is concerned.

Grødem

In the trade magazine ScanRef (Scandinavian Refrigeration 3/98) Bjørn Grødem, also from Norway, states that the above price differences are somewhat lower. Grødems statement is based on German investigations of refrigeration systems for supermarkets, where comparisons between indirect cooling with R-404A, ammonia and hydrocarbons have been made. Prices have been compared with a direct R-404A refrigeration system as well.

Table B.1: Price comparison between different types of supermarket systems. According to Grødem, ScanRef 3/98. Index 100 is the value for direct cooling with R-404A.

|  | Direct system using R404a | Indirect system using R-404A | Indirect system using ammonia | Indirect system using propane/ propene |
| --- | --- | --- | --- | --- |
| Pipe system | 15% | 25-30% | 25-30% | 25-30% |
| Refrigeration cabinets and air coolers | 45% | 45% | 45% | 45% |
| Refrigeration system | 20% | 25% | 34-40% | 23-28% |
| Refrigerant, oil and brine | 2% | 2% | 2% | 2% |
| Control and electrical installation | 15% | 15% | 16% (extra for safety) | 17% (extra for safety) |
| Planning | 3% | 3% | 3% | 3% |
| Price | 100% | 115-120% | 125-135% | 115-125% |

As can be seen in table B.1, direct refrigeration systems are the most competitive. In addition, only a limited price difference between the indirect systems appears. In particular, only a small price difference (a minor percentage of the total costs of system) appears when comparing the R-404A and the hydrocarbon system.

Estimation of prices for hydrocarbon refrigeration systems

In co-operation with Alexander C. Pachai, AirCon A/S, Denmark, DTI Energy has made an analysis of future prices for hydrocarbon systems compared with a similar HFC refrigeration system.

The analysis assumes a large-scale production of the hydrocarbons systems similar to the present production of HFC refrigeration systems, thus achieving large-scale production benefits. The analysis also assumes that authorities have issued explicit guidelines on the building of hydrocarbon systems and that fitters have been properly trained in handling hydrocarbons. These requirements prevail in Sweden, where the company Bonus Energy AB builds hydrocarbon refrigeration systems, but not in other Nordic countries.

Components

Most of the components used in a hydrocarbon system are similar to the ones used in an HFC refrigeration system, and thus the price level will be identical. However, a certain price difference prevails for automatic controls. Application of explosion-safe components like differential pressure controllers, thermostats, terminal boxes, relays and ventilators, registered in the IP 44 safety category, is demanded. In Denmark the IP 23 safety category is normally used for commercial refrigeration systems, but this category is not sufficient for use of hydrocarbons. An example of a 14 kW refrigeration system is shown in chapter B.3, where the prices of component are shown as well. From this example a 4.3% price difference occurs, however this difference will be reduced for large systems.

Assembling

In hydrocarbon systems all joints and connections must be soldered. HFC refrigeration systems may be connected either by means of soldering or by use of screw fittings. Although the soldering process will require more working hours, this is expected to be equalised by decreased material consumption (i.e. screw fittings). Additional costs are expected in the range of 0 - 1%. The time used for leak detection is similar to that used for an HFC refrigeration system.

Safety

In the case of indoor machine room installation of the refrigeration system, the presence of a gas alarm at ground level is required. In case of outdoor or semi-roof installation, this precaution may not be necessary. The same requirements are valid for an HFC refrigeration system, which ought also to include a refrigerant leakage detector. The price for a gas alarm and the associated  ventilator amounts to approximately DKK 6000 (list price).

Education

To secure that fitters are duly skilled for proper handling of hydrocarbons, establishment of a training system is required. Until now this is only the case in Sweden.

Equipment

For proper hydrocarbon handling, the assembling company needs suitable equipment.

The price of a hydrocarbon leak detector is almost similar to the one required for artificial refrigerants, e.g. HFC, which is also the case with a hydrocarbon charging aggregate. In addition, an explosion-safe vacuum pump is required, the price of which will be approximately 50% higher than the price of a traditional pump (list price is approximately DKK 7150).

For some time, the Danish transport requirements for pressure bottles containing hydrocarbon refrigerant have been the cause of confusion. According to previous advice issued by the Danish Society for Gas Technology, gas bottles should be placed in safety rooms in the service cars. Consequently, the requirements will differ from those of other gas bottles, e.g. acetylene for welding and soldering processes. At the moment, DTI Energy is investigating these requirements.

Conclusion

It has been concluded that the price of hydrocarbon systems is somewhat higher than that of similar HFC refrigeration systems. The price difference ranges between 10-40%, however, nothing will prevent a significant decrease of this in the future. Compared to a HFC refrigeration system, components for a 14 kW output hydrocarbon system are about 5% more expensive. In addition, due to the assembling process a 1% price increase will appear, including a possible additional charge for detector installation. However, use of detector is also recommended for HFC refrigeration systems.

Supermarket hydrocarbon refrigeration must be carried out by means of indirect cooling. Thus, the difference from an HFC refrigeration with direct system systems becomes more significant.

Estimation of future prices for ammonia refrigeration systems

Today ammonia refrigeration systems are competitive when taking systems larger than 100 kW into consideration. However, this is not yet the case with small and medium sized refrigeration systems, a fact, which can be changed. Not until recently has the use of ammonia in small and medium sized refrigeration systems been in focus and the number of available compressors is increasing.

However, the price level of these continues to be higher compared to prices of similar compressors for HFC refrigerants, but it is likely to believe that price equalisation will be generated by means of production of larger quantities. Furthermore, as far as pipe systems are concerned, new assembling methods are being developed to obtain lockring or fittings as an alternative to soldering.

B.2 Energy consumption and TEWI for commercial refrigeration systems based on supermarket refrigeration systems

From January 1994 the assembling of new commercial refrigeration systems using CFC refrigerant (CFC-12, R-502 etc.) was prohibited in Denmark. In new refrigeration systems the use of HCFC will be prohibited from January 2000. From January 2002 this will include application of new HCFC for service purposes as well.

Hence, HFC based refrigerants including HFC-134a, R-404A or possibly R-407 are used in most of the new supermarket cooling cabinets and other commercial refrigeration systems.

Direct cooling is used in supermarkets in Denmark and Norway, whereas the use of indirect cooling is becoming more frequent in Sweden, Germany and other countries. In Sweden new supermarket refrigeration systems must be provided with indirect cooling. According to the Swedish Refrigeration Standard, a partly indirect refrigeration system is required for filling charges between 10 and 30 kg. Traditionally, an indirect system will be used for cooling and a direct system will be used for freezing.

Filling charges over 30 kg require a completely indirect system, i.e. indirect systems for both cooling and freezing.

For direct supermarket cooling, liquid refrigerant will flow in long pipe systems to the cooling places, e.g. cooling or freezing storage, milk cooling cabinets, cold stores etc. Afterwards the evaporated refrigerant is led back in other pipe systems. In a medium sized supermarket, with cooling required at 30-40 different locations, there are often kilometres of refrigerant pipes and hundreds of pipe connections.

A certain amount of leakage is almost impossible to avoid in these pipe systems. Leakage will often occur in valve gaskets and connections, or by direct accident caused by broken pipes. Previously, the assumed leakage rate of these systems amounted to 20-30% of the annual filling charge.

Great efforts have been made within the trade to improve the quality of new systems, and hence a considerable reduction of the leakage rate is assumed. IPCC’s guidelines from 1996 state an annual average leakage rate of 17%. However, a 100% tightness of the systems is not technically possible. The exact figures are not known, however an annual 10% leakage rate for supermarket systems with direct cooling is assumed.

It is less expensive to produce a refrigeration system with direct cooling than a similar system using indirect cooling. According to Haukås the price is 20% higher, whereas Grødem mentions a 15-20% price increase of the indirect system.

This price difference is due to the slightly higher prices for pipe systems. Investment in circulation pumps for the secondary refrigerant is necessary. In addition, investment in additional heat exchangers between the primary and secondary system is required.

On the other hand a considerably smaller amount of refrigerant is required (often 15-20% depending on the amount in a direct system) and the leakage rate will be much less, often only 5%.

Energy consumption

The precise energy consumption in the various systems is hard to predict, as it depends on the retrofitting rate of the individual systems. However, Bjørn Grødem has tried to estimate some figures in ScanRef 3/98, which are as follows:

Table B.2: Energy consumption for different supermarket refrigeration systems. The source is similar to that used in table B.1. However, it should be emphasised that this example is not necessarily valid for all systems.

|  | Direct system using R404A | Indirect system using R404A | Indirect system using propane/ propene | Indirect system using NH3 (ammonia) |
| --- | --- | --- | --- | --- |
| Estimated energy consumption | 100% | 110% | 108% | 105% |

The energy consumption is slightly higher for the indirect systems due to the thermodynamic loss from temperature differences in the heat exchanger between the primary and secondary refrigeration system and the pumps’ energy consumption. This will to some extent be balanced by improved efficiency of the hydrocarbon and the ammonia refrigeration system.

It is estimated that the design of hydrocarbon refrigeration systems soon will result in energy consumption for indirect systems, which does not exceed the consumption for direct systems. Use of components (compressors), which have been optimised according to the refrigerant, is required. Previously, R-22 components for propane or propene have been used. Through this optimisation the difference between direct HFC systems and indirect hydrocarbon systems will be significantly less.

New secondary refrigerants will be available on the market in the future, including ice slurry for refrigeration purposes and CO2 for freezing purposes. Hence, in comparison with direct HFC systems an improvement of the energy consumption used for indirect systems using ammonia or hydrocarbons is expected.

Contribution to the green house effect, TEWI

Refrigeration systems contribute both directly and indirectly to the green house effect. Direct contribution is caused by leak of refrigerant, e.g. R-404A, which has a GWP (Global Warming Potential) of 3260, compared to CO2, which has a GWP of 1.

The indirect contribution derives from electricity consumption. If electricity is generated at coal fired power plants, as is the case in Denmark, the CO2 emission from the power plant’s stack corresponds to 0.8 kg of CO2 per kWh of electricity.

The TEWI value (Total Equivalent Warming Impact) combines both 					direct and indirect  contributions, i.e.:

TEWI = GWP * M + ALFA * E

where

GWP is the GWP factor of the refrigerant;

M is the amount of refrigerant, leaking from the refrigeration system;

ALFA is the amount of CO2, which is generated during electricity production (kg of CO2 per kWh);

E is the electricity consumption of the refrigeration system.

Example

An example of a typical supermarket refrigeration system is given below. The example, which is typical for countries with direct cooling as standard, comprises a medium sized supermarket (e.g. Danish supermarket such as Kvickly, Føtex) with a sales area of 1000-1500 m2.

The total refrigeration efficiency is 100 kW and the system is provided with direct cooling. The refrigerant charge is 300 kg of R-404A.

The annual energy consumption of the refrigeration system is 170,000 kWh, whereas the leakage rate is 10% of the annual charge, i.e. 30 kg.

TEWI calculation stating yearly operation of the refrigeration system:

Direct yearly contribution to the green house effect:

M * GWP = 30 kg of R-404A * 3260 (kg of CO2/kg of R-404A) = 97800 kg of CO2 = 97.8 tonnes of CO2.

Indirect contribution to the green house effect: ALFA * E = ALFA * 170,000 kWh.

Table B.3: Contribution to the green house effect for the refrigeration system stated in the example. This example is for direct cooling with R-404A.

|  | ALFA (kg of CO2/kWh) | Indirect contribution to the green house effect (kg of CO2) | Direct contribution to the green house effect (kg of CO2) | TEWI for one year (kg of CO2) |
| --- | --- | --- | --- | --- |
| Coal-firing | 0.8 | 136.000 | 97.800 | 233.800 |
| 100% hydro- electric power (or nuclear power) | 0 | 0 | 97.800 | 97.800 |
| 50% coal power + 50% hydroelectric power | 0.4 | 68.000 | 97.800 | 165.800 |

According to the example the 100% coal-fired power station accounts for the direct contribution to the green house effect (approximately 42% of the total TEWI contribution).

In the example with 50% coal and 50% hydroelectric power supply the share accounts for 59%. According to the example the share of hydroelectric power supply accounts for 100%. It should be mentioned that other environmentally related problems occur in connection with hydroelectric and nuclear power. In this example only the green house effect is included.

It has often been said that the refrigerant share of the TEWI value is very limited. However, this does not seem to be the case with supermarket refrigeration systems using R-404A and direct cooling. The refrigerant accounts for a considerable share of the total impact of the green house effect.

When using a hydrocarbon or an ammonia refrigeration system in the same supermarket, a considerably lower green house impact will be achieved, despite the small increase of energy consumption shown in the following table.

Table B.4: The TEWI value for a supermarket refrigeration system using propane and indirect cooling, c.f. table B.3. It should be mentioned that calculations are only related to the contribution to the green house effect. This example may not necessarily be representative for other commercial refrigeration systems.

|  | ALFA (kg of CO2/kWh) | Indirect contribution to the green house effect (kg of CO2) | Direct contribution to the green house effect (kg of CO2) | TEWI (kg of CO2) | TEWI (R290) / TEWI (R-404A) |
| --- | --- | --- | --- | --- | --- |
| Coal-firing | 0.8 | 146.880 | 0 | 146.880 | 0.63 |
| 100% hydroelectric | 0 | 0 | 0 | 0 | 0 |
| 50% coal- firing 2 50% hydroelectric | 0.4 | 73.440 | 0 | 73.440 | 0.44 |

According to the values shown in table B.4 the total impact of the green house effect is far lower for a hydrocarbon or ammonia refrigeration system using indirect cooling than for an R-404 refrigeration system using direct cooling. The result is independent of electricity production methods.

B.3 Differences in traditional and in hydrocarbon refrigeration systems

In this chapter the price differences between components for HFC and hydrocarbons systems are described.

Components in a traditional refrigeration system

The design of a traditional refrigeration system is often very simple. In many cases a thermostat equipped with an on/off signal is used. If the system is provided with an air-cooled condenser, application of a differential pressure controller to obtain suitable condensing pressure during cold intervals is frequently used.

Most of the components that can ignite a spark are categorised under the protection classification IP 23 or the like, which also implies fans. In many cases the terminal box of the compressor, which contains the starting relay or other relays than can cause a spark, are included as well. In Denmark no rules concerning the application of twin diaphragm differential pressure control for chemical refrigerants prevail. As a consequence, these are not commonly used, although their application may reduce emission of potent green house gases. This is also the explanation of their extent of use in Germany.

Price differences between IP 23 and IP 44 or above

In connection with hydrocarbon refrigeration systems it is required as a minimum that equipment is categorised under the safety classification of at least IP 44 or even above. IP 54 and IP 55 are becoming a standard, wherefore products of this class are normally easily obtained.

The definition of safety classification requires some knowledge about the relevant nomenclature. Briefly, on a scale from 0 to 6 the first number indicates dust-proofness. The second number indicates water-proofness also on a scale from 0 to 6. Thus, an apparatus categorised under IP 23 is not quite dustproof and will only tolerate water spray, whereas an apparatus under IP 66 remains tight when exposed to water through a certain period and depth. Further details concerning this matter is described in an European standard.

Considering the system mentioned in the example, prices are indicated in the following table for a system provided with a suitable casing and improved level of safety.

Table B.5: Comparison between components for a traditional HFC refrigeration systems and similar hydrocarbon systems. The refrigeration performance is app. 14 kW.

| Component | List price | Alternative | List price |
| --- | --- | --- | --- |
| KP 15 Flare (pressure controller) | DKK 483.00 | KP 17 W Soldered | DKK 700.00 |
| KP 5 Flare (pressure controller) | DKK 261.00 | KP 7 W Soldered | DKK 474.00 |
| KP 73 (2 pcs.) (thermostat) | DKK 742.00 | RT 2 (2 pcs.) | DKK 1,640.00 |
| Compressor aggregate UAK 500 | DKK 24,992.00 | Same | DKK 24,992.00 |
| TAU plate heat exchanger | DKK 4,330.00 | Same | DKK 4,330.00 |
| Total price | DKK 30,808.00 | Total price | DKK 32.136.00 |

According to the example, a slight price difference appears for the entire system.

Whereas the price of some components in the high protection class is more than twice as much as the others, the most expensive components in the system are not more expensive, thus eliminating to some degree the price difference. The same type of components is used despite the size of system. Should the price of compressor, condenser and evaporator be more than doubled, the additional price for the subcomponents will be insignificant compared to the total price. According to the example, only a 5% price difference for the components alone is registered.

However, it should be emphasised that apart from Sweden the end-users in the Nordic countries may choose between an HFC refrigeration system with direct cooling and a hydrocarbon using indirect cooling. In this case the price difference will be higher, see table B.1.

As Swedish systems traditionally use indirect cooling. a lower price difference will be registered in this case.

# Appendix C:  Sabroe Chillers with NH3-refrigerant, installed in Denmark 1990-1998

Installed	Refrigeration capacity

Lego A/S, Billund					1990		2.000 kW

Grindsted Products, Grindsted			1990		470 kW

Statens Seruminstitut, Copenhagen			1990		125 kW

The Copenhagen Mail Centre, Copenhagen		1992		800 kW

Novo Nordisk, Kalundborg + 5 other chillers		1992		2.800 kW

MD Foods, Troldhede Dairy	, Troldhede		1993		55 kW

MD Foods, HOCO, Holstebro			1993		2.000 kW

SAS Data, Kastrup					1993		2 x 155 kW

Panum Institute, Copenhagen University		1993		920 kW

National Hospital of Denmark, Copenhagen		1993		1.000 kW

Toyota, Middelfart			          		1993		360 kW

Scandinavian Center, Aarhus			1993          	1.000 + 800 kW

SAS Data, Copenhagen				1994		155 kW

Danaklon, Varde					1994		520 kW

Dandy, Vejle					1994		3 x 1.000 kW

EAC, Head Office, Copenhagen			1994		1.100 kW

Copenhagen Pectin, Lille Stensved			1994		230 kW

Novo Nordisk, Kalundborg				1994		340 kW

SAS Data, Kastrup					1994		2 x 155 kW

Rødovre Skating Rink, Rødovre			1994		500 kW

SDC of 1993 A/S,	Ballerup				1994		1.600 kW

Dandy,Vejle					1995		800 kW

Danish National Television, Head Office, Cph.		1995		850 kW

Copenhagen Airport, Copenhagen			1995		1.066 kW

Magasin (Dept. Store), Aalborg			1995		528 kW

Schou-Epa (Dept. Store), Roskilde			1995		175 kW

Lundbech A/S, Lumsås				1995		500 kW

Løvens Kemiske Fabrik, Ballerup			1995		174 kW

Faxe Kalk, Fakse					1995		686 kW

PBS Finans A/S, Ballerup				1995 + 1997	640 kW

Schouw Packing A/S, Lystrup			1995		397 kW

Pharmacia, Køge					1995		76 kW

NKT Project Center, Kalundborg			1995		340 kW

Aalborg Storcenter (Dept. Store), Aalborg		1995		2.530 kW

Nordisk Wawin A/S, Hammel			1996		200 kW

Novo Nordisk, Gentofte				1996		100 kW

Kastrup Stationsterminal, Kastrup			1996		804  kW

Novo Nordisk, Gentofte				1996		1.096 kW

J & B Enterprise A/S, SID Building			1996		162,4 kW

Novo Nordisk (Building  3A-Ba), Bagsværd		1996		370 kW

Novo Nordisk (Building AE-KA), Bagsværd		1996		200 kW

Danisco Foods A/S, Odense				1996		220 kW

SDC of 1993 A/S, 	Ballerup				1996		1.588 kW

Copenhagen Airports, Copenhagen			1996		185 kW

Risø National Laboratory, Roskilde			1996		1.820 kW

Codan Gummi A/S, Køge				1996		175 kW

Magasin du Nord (Dept. Store), Copenhagen		1996		528 kW

Glent Novenco, Åbyhøj				1996		50 kW

Superfos Packing A/S, Hårby			1996		495 kW

Dandy, Vejle					1996		3.560 kW

Palsgård Industri A/S, Juelsminde			1996		25 kW

Aarhus Oliefabrik A/S, Aarhus			1996		406 kW

Danisco A/S, Copenhagen				1996		270 kW

H. C Ørsted Institute, Copenhagen University		1996		254 kW

Eberhart A/S, Engesvang				1996		261 kW

Danisco Ingredients, Copenhagen			1996		45 kW

Kastrup Skating Rink, Kastrup			1996		583 kW

Lundbech A/S, Valby				1997		500 kW

Hvidovre Hospital, Hvidovre			1997		2 x 2.543 kW

Nordisk Wavin, Hammel				1997		202 kW

H.C. Ørsted Institute, Copenhagen University		1997		254 kW

Novo Nordisk, Bagsværd				1997		200 kW

Copenhagen Airports (Finger B), Copenhagen		1997		2 x 804 kW

Copenhagen Airports (Finger Vest), Copenhagen		1997		900 kW

Novo Nordisk, Hillerød				1997		3.840 kW

Delta A/S, Hørsholm				1997		130 kW

Ishøj Bycenter, Ishøj				1997		1.030 kW

Unibank, Christianshavn				1997		538 kW

Copenhagen Pectin A/S, Lille Stensved		1997		530 kW

Illum A/S (Dept. Store), Copenhagen			1997		1.022 kW

Scandic Hotel Copenhagen, Copenhagen		1997		359 kW

Tholstrup Gjesing A/S, Skanderborg			1997		395 kW + 53 kW

Tjæreborg Champignon, Tjæreborg			1997		1.146 kW

MD Foods, Troldhede Dairy	, Rødkærsbro		1997		240 kW

Eghøj Champinon A/S, Veflinge			1997		500 kW

Danisco Distillers, Aalborg				1997		9 kW

FeF Chemicals A/S, Køge				1997		68 kW

Novo Nordisk - Building 3BM-Ba, Bagsværd		1997		129 kW

Phønix Contractors A/S, Vejen			1997		575 kW

SDC af 1993 A/S, 	Ballerup				1997		505 kW

Hørsholm Skating Rink, Hørsholm			1998		370 kW

Novo Nordisk A/S	, Gentofte			1998		1.670 kW

Søndagsavisen, Copenhagen				1998		80 kW

Løvens Kemiske Fabrik, Ballerup			1998		300 kW

Nordisk Wawin, Hammel				1998		220 kW

Schulstad, Holstebro				1998		290 kW

Løvens Kemiske Fabrik, Ballerup			1998		320 + 120 kW

Birch & Krogboe A/S, Virum			1998		390 + 50 kW

MD Foods, Bislev, Bislev				1998		1.500 kW

Albani, Odense					1998		270 kW

Mejeriernes Produktionsselskab, Esbjerg		1998		400 kW

Hvide Sande Fiskeriforening, Hvide Sande		1998		100 kW

Løvens Kemiske Fabrik, Ballerup			1998		2 x 214 kW

Copenhagen Airports, Copenhagen			1998		660 kW

Novo Nordisk A/S, Kalundborg			1998		100 kW + 2 x 400 kW

Tulip, Århus					1998		70 kW

Scandinavian Air Lines, Copenhagen			1998		160 kW

Ørbæk Most, Ørbæk				1998		120 kW

Danexport, Hobro					1998		650 kW

Marine Biologisk Institut				1998		2 x 30 kW

# Appendix D: Gram Chillers (York International) with NH3 refrigerant, installed in Denmark 1992-1998

|  | Prodution | Refrigeration capacity |
| --- | --- | --- |
| Force Institutes Brøndby | Containerised water chiller for process chilling of welding machines | 200 kW |
| Esbjerg Thermoplast Esbjerg | Water chillers for process chilling of plastic moulding plant | 2 x 187 kW |
| Sun Chemical Køge | Water chillers for process chilling in chemical industry | 235 kW |
| Magasin Department Store Copenhagen | Water chiller for A/C | 2 x 907 kW |
| Vellev Dairy Vellev | Brine (glycol) chiller for process chilling (ice water) | 225 kW |
| Chr. Hansens Lab. Roskilde | Walter chiller for process chilling of pharmaceutical laboratories | 407 kW |
| Tele Danmark Odense | Water chiller for A/C of main telephone central | 3 x 232 kW |
| Danish State Hospital Copenhagen | Brine (glycol) chiller for refrigeration & freezing of central kitchen facilities | 52 kW |
| Magasin Department Store Aarhus | Water chiller for A/C | 1.449 kW |
| Esbjerg City Hall Esbjerg | Water chiller for A/C | 540 kW |
| County Data Odense | Water chillers for A/C | 2 x 195 kW |
| Frederiksberg Hospital Copenhagen | Water chiller for A/C | 322 kW |
| Esbjerg Hospital Esbjerg | Water chiller for A/C | 2 x 554 kW |
| Esbjerg Hospital Esbjerg | Water chiller for A/C | 868 kW |
| Panther Plast Vordingborg | Water chillers for process chilling of plastic moulding plant | 2 x 602 kW |
| Printca Aalborg | Water chillers for process chilling in pharmaceutical industry | 322 kW |
| ATP House Hillerød | Water chiller for EDP cooling and ventilation | 180 kW |
| Berlingske Newspaper- Production Avedøre | Water chillers for A/C | 2 x 919 kW |
| H. Lundbeck Pharmaceutical Valby | Water chiller for process chilling in pharmaceutical industry | 994 kW |
| ATP House Hillerød | Water chiller for EDP cooling and ventilation | 564 kW |
| Copenhagen Airport Kastrup | Water chiller for ventilation in luggage sorting | 350 kW |
| Grundfos Bjerringbro | Containerised liquid chiller for test plant | 25 kW |
| NeuroSerch A/S Ballerup | Water chiller for process chilling in pharmaceutical industry | 400 kW |
| Technos Schou A/S Vamdrup | Brine chiller for process chilling at painting production | 175 kW |
| Jyske Avistryk A/S Kolding | Water chiller for process chiller for printing machines | 450 kW |
| P-Industri Bjæverskov | Water chiller for plastics industry | 240 kW |
| Sophus Berendsen Søborg | Water chillers for ventilation | 284 kW |

# Appendix E: Bonus Chillers with Hydrocarbon-refrigerant, installed in Sweden 1996-1998

Installed	Refrigeration capacity

Bäckhammars Bruk, Kristinehamn			1996		19 kW

Vasakronan Real estate, Norrköping			1996		2 x 260 kW

AG’s Favör, Lund					1996		3 x 192 kW

AG’s Favör, Lund					1996		2 x 50 kW

AG’s Favör, Landskrona				1996		2 x 128 kW

AG’s Favör, Landskrona				1996		25 kW

Ronneby Real Estate, Bräkne-Hoby			1996		2 x 250 kW

TA Hydronics, Göteborg				1996		66 kW

ABB Real Estate,	Enköping			1996		60 kW

Pharmacia & Upjohn, Uppsala			1996		40 kW

The Birgitta Gymnasium, Örebro			1996		10 kW

Hållstugan Daycare center, Örebro	      		1996		38 kW

Melkers meat processing, Falun			1996		76 kW

Ljungby Hospital, 	Ljungby				1996		2 x 298 kW

Calor Gas, GB					1996		2 x 600 kW

NWT - Newspaper, Karlstad				1996		2 x 298 kW

SEAB Gävle, Gävle				1996		20 kW

Areng Spa, Italien					1996		3 kW

Binsell, Uppsala					1996		46 kW

AG’s Favör, Helsingborg				1997		4 x 120 kW

AG’s Favör, Helsingborg				1997		3 x 228 kW

Domus (COOP), Visby				1997		2 x 40 kW

Domus (COOP), Visby				1997		2 x 126 kW

ASSI Domän, Frövi				1997		95 kW

ASSI Domän, Frövi				1997		28 kW

Edbergs, 	Örebro					1997		38 kW

University of Luleå, Luleå				1997		82 kW

Akzo-Nobel, Ömsköldsvik				1997		91 kW

Volvo, Köping					1997		6 x 336 kW

Hällstugan Daycare center, Örebro			1997		38 kW

ASSI Domän, Frövi				1997		95 kW

ASSI Domän, Falum				1997		82 kW

ABB Atom, Västerås				1997		164 kW

Pastejköket, Tranås				1997		3 x 216 kW

SKV, Svängsta					1997		10 kW

County of Karlstad, Karlstad			1997		2 x 260 kW

Katedral gymnasium, Skara				1997		111 kW

IUC-Gymnasium,	Katrineholm			1997		20 kW

Saluhallen, Uppsala				1997		82 kW

Saluhallen, Uppsala				1997		54 kW

ICA HQ,	 Västerås					1997		190 kW

Volvo Aero, Arboga				1997		48 kW

Volvo Aero, Arboga				1997		95 kW

Hospital of Skellefteå, Skellefteå			1997		2 x 260 kW

Hospital of Skellefteå, Skellefteå			1997		2 x 56 kW

Hospital of Skellefteå, Skellefteå			1997		8 kW

Swedish Road Adm., Borlänge			1997		2 x 56 kW

ASSI Domän, Frövi				1997		41 kW

Ericsson, Ursviken					1997		2 x 190 kW

Swedish Army, Visby				1997		111 kW

County of Gävle, Bollnäs				1997		4 x 520 kW

County of Gävle, Bollnäs				1997		34 kW

TA Hydronics, Göteborg       			1997		69 kW

Real Estate Company, Umeå   			1997		2 x 96 kW

ASSI Domäm, Frövi                    			1997		20 kW

Hospital of  Lindesberg, Lindesberg			1997		20 kW

Hospital of Söderhamn, Söderhanm			1997		20 kW

Swedish Road Adm, Örebro				1997		170 kW

Electrolux, Holland				1997		5 kW

University of Umeå, Umeå				1997		10 kW

Swedish Coast Artillery, Stockholm			1997		2 x 56 kW

Vombverket, Veberöd				1998		2 x 160 kW

Hospital of Linköping, Linköping			1998		2 x 86 kW

Swedish Radio, Luleå				1998		122 kW

Hospital of Sandviken, Sandviken			1998		34 kW

Country of Karlstad, Karlstad			1998		122 kW

Country of Karlstad, Karlstad			1998		90 kW

Umeå gymnasium, Umeå				1998		2 x 138 kW

ABB Atom, Västerås				1998		21 kW

House of Wasa, Örebro				1998		2 x 180 kW

Nestlé, Malmö					1998		78 kW

Unikum in Örebro,	 Örebro				1998		2 x 244 kW

Kv Sjövik, Stockholm				1998		122 kW

Country of Karlstad, Karlstad			1998		60 kW

ABB Atom, Västerås				1998		180 kW

Sparebanken, Köping				1998		2 x 206 kW

Kv Harren, Luleå					1998		122 kW

Expolaris, Skellefteå				1998		38 kW

University of Karlstad, Karlstad			1998		34 kW

University of Karlstad, Karlstad			1998		147 kW

Hospital of Ljungby, Ljungby			1998		147 kW

Vasakronan Real estate, Norrköping			1998		122 kW

TÜV-approval, Tyskland				1998		90 kW

Fire Brigade, Luleå				1998		33 kW

Sabroe + Søby, Danmark				1998		90 kW

# Text boxes

Natural   refrigerants

Different categories

The CFC group under Danish Industries

Nordic report

Secondary refrigerants

Svensk Kylnorm

##### Ice slurry

Denmark, hydrocarbons

Future refri-

geration plants

Cold air refrigeration system in trains

##### Hydrocarbons

Shortage of HCFC-141b

##### Milk Cooling

##### Isopentane

SO2